## Pumped Well Info
WELL, TEST, AQUIFER INFORMATION FOR PUMPING WELL
Well Information |  | Test Information |  | Aquifer Information
Well Name: | Saanich South Well | Date of start of test (yyyy-mm-dd): | 2022-08-23 | Aquifer Number: | 614
Well ID Plate Number: | 32192 | Type of test (step test, constant rate test): | constant rate test | Aquifer Lithology | Granite (Karmutsen Formation)
Well Tag Number: | 54024 | SWL at start of test (m): | 0.721 | Aquifer Type: | Fractured Crystalline Bedrock
Well Location : | Tsartlip First Nation | Reference datum for water level measurements (top of production casing): |  | Depth to upper-most water bearing fracture (m) | 24.4
UTM Zone (easting, northing): |  | Datalogger water level measurements?: | Yes
Well Casing Inside Diameter (mm): | 159 | Was a step-drawdown test performed before the constant rate test? | No
Driller's Well Record (image):

## Pumped Well Data
Pumped Well Data
WTN | 54204 | SWL (m): | 0.721 |  | Average Pumping Rate (m3/day): |  |  | 38.02
Derivative is very noisy due to the amplification of small measuments errors. Derivative will be easier to interpret with a greater L-spacing inverval (L=8 was chosen)
Time since pumping started, t (min) | Time since pumping stopped, t' (min) | t/t' | Pumping rate, Q (USgpm) | Pumping rate, Q (L/s) | Pumping Rate, Q (m3/day) | Water Level (ft) | Water Level (m) | Drawdown or Residual Drawdown (m) | Extended Drawdown (m) | ln(t) | Dt1 | Dt2 | Ds1 | Ds2 | ds/dt | Dt1 | Dt2 | Ds1 | Ds2 | ds/dt (L-Spacing = 8) | d2s/dt2
4 | - | - | 7 | 0.44163 | 38.02 | 12.1275 | 3.6963 | 2.9749 | 2.9749 | 1.3863 | #REF! | 0.81093 | #REF! | 1.5425 | #REF!
9 | - | - | 7 | 0.44163 | 38.02 | 17.1884 | 5.2388 | 4.5174 | 4.5174 | 2.1972 | 0.81093 | 0.44183 | 1.5425 | 0.9699 | 2.0918 | 1.6946 | 0.59682 | 3.5683 | 0.92803 | 1.6984
14 | - | - | 7 | 0.44163 | 38.02 | 20.3706 | 6.2087 | 5.4873 | 5.4873 | 2.6391 | 0.44183 | 0.30538 | 0.9699 | 0.66073 | 2.1765
19 | - | - | 7 | 0.44163 | 38.02 | 22.5385 | 6.8694 | 6.148 | 6.148 | 2.9444 | 0.30538 | 0.23361 | 0.66073 | 0.4863 | 2.1172
24 | - | - | 7 | 0.44163 | 38.02 | 24.134 | 7.3557 | 6.6343 | 6.6343 | 3.1781 | 0.23361 | 0.18924 | 0.4863 | 0.40108 | 2.1025
29 | - | - | 7 | 0.44163 | 38.02 | 25.45 | 7.7568 | 7.0354 | 7.0354 | 3.3673 | 0.18924 | 0.15906 | 0.40108 | 0.32065 | 2.0632
34 | - | - | 7 | 0.44163 | 38.02 | 26.502 | 8.0774 | 7.3561 | 7.3561 | 3.5264 | 0.15906 | 0.1372 | 0.32065 | 0.27256 | 2.0002
39 | - | - | 7 | 0.44163 | 38.02 | 27.3963 | 8.35 | 7.6286 | 7.6286 | 3.6636 | 0.1372 | 0.12063 | 0.27256 | 0.23599 | 1.9705
44 | - | - | 7 | 0.44163 | 38.02 | 28.1706 | 8.586 | 7.8646 | 7.8646 | 3.7842 | 0.12063 | 0.10763 | 0.23599 | 0.22109 | 2.0081
49 | - | - | 7 | 0.44163 | 38.02 | 28.896 | 8.8071 | 8.0857 | 8.0857 | 3.8918 | 0.10763 | 0.097164 | 0.22109 | 0.18887 | 1.9962 | 0.59682 | 0.37118 | 0.92803 | 0.58445 | 1.5671
54 | - | - | 7 | 0.44163 | 38.02 | 29.5157 | 8.9959 | 8.2746 | 8.2746 | 3.989 | 0.097164 | 0.088553 | 0.18887 | 0.17378 | 1.9536
59 | - | - | 7 | 0.44163 | 38.02 | 30.0859 | 9.1697 | 8.4484 | 8.4484 | 4.0775 | 0.088553 | 0.081346 | 0.17378 | 0.084986 | 1.4841
64 | - | - | 7 | 0.44163 | 38.02 | 30.3647 | 9.2547 | 8.5333 | 8.5333 | 4.1589 | 0.081346 | 0.075223 | 0.084986 | 0.077843 | 1.0396
69 | - | - | 7 | 0.44163 | 38.02 | 30.6201 | 9.3326 | 8.6112 | 8.6112 | 4.2341 | 0.075223 | 0.069959 | 0.077843 | 0.095206 | 1.2038
74 | - | - | 7 | 0.44163 | 38.02 | 30.9325 | 9.4278 | 8.7064 | 8.7064 | 4.3041 | 0.069959 | 0.065383 | 0.095206 | 0.090457 | 1.3726
79 | - | - | 7 | 0.44163 | 38.02 | 31.2293 | 9.5182 | 8.7968 | 8.7968 | 4.3694 | 0.065383 | 0.061369 | 0.090457 | 0.11154 | 1.6073
84 | - | - | 7 | 0.44163 | 38.02 | 31.5952 | 9.6298 | 8.9084 | 8.9084 | 4.4308 | 0.061369 | 0.05782 | 0.11154 | 0.10535 | 1.8198
89 | - | - | 7 | 0.44163 | 38.02 | 31.9409 | 9.7351 | 9.0137 | 9.0137 | 4.4886 | 0.05782 | 0.054658 | 0.10535 | 0.089038 | 1.7228 | 0.37118 | 0.27009 | 0.58445 | 0.45135 | 1.6305
94 | - | - | 7 | 0.44163 | 38.02 | 32.233 | 9.8241 | 9.1028 | 9.1028 | 4.5433 | 0.054658 | 0.051825 | 0.089038 | 0.083745 | 1.6223
99 | - | - | 7 | 0.44163 | 38.02 | 32.5078 | 9.9079 | 9.1865 | 9.1865 | 4.5951 | 0.051825 | 0.049271 | 0.083745 | 0.082614 | 1.6471
104 | - | - | 7 | 0.44163 | 38.02 | 32.7788 | 9.9905 | 9.2691 | 9.2691 | 4.6444 | 0.049271 | 0.046957 | 0.082614 | 0.067361 | 1.5527
109 | - | - | 7 | 0.44163 | 38.02 | 32.9998 | 10.0579 | 9.3365 | 9.3365 | 4.6913 | 0.046957 | 0.044851 | 0.067361 | 0.066278 | 1.4566
114 | - | - | 7 | 0.44163 | 38.02 | 33.2173 | 10.1241 | 9.4028 | 9.4028 | 4.7362 | 0.044851 | 0.042925 | 0.066278 | 0.064747 | 1.4934
119 | - | - | 7 | 0.44163 | 38.02 | 33.4297 | 10.1889 | 9.4675 | 9.4675 | 4.7791 | 0.042925 | 0.041158 | 0.064747 | 0.068278 | 1.5852
124 | - | - | 7 | 0.44163 | 38.02 | 33.6537 | 10.2572 | 9.5358 | 9.5358 | 4.8203 | 0.041158 | 0.039531 | 0.068278 | 0.062392 | 1.6178
129 | - | - | 7 | 0.44163 | 38.02 | 33.8585 | 10.3196 | 9.5982 | 9.5982 | 4.8598 | 0.039531 | 0.038027 | 0.062392 | 0.060916 | 1.5903 | 0.27009 | 0.21244 | 0.45135 | 0.34971 | 1.6572
134 | - | - | 7 | 0.44163 | 38.02 | 34.0583 | 10.3805 | 9.6591 | 9.6591 | 4.8978 | 0.038027 | 0.036634 | 0.060916 | 0.055484 | 1.5574
139 | - | - | 7 | 0.44163 | 38.02 | 34.2404 | 10.436 | 9.7146 | 9.7146 | 4.9345 | 0.036634 | 0.035339 | 0.055484 | 0.059694 | 1.6034
144 | - | - | 7 | 0.44163 | 38.02 | 34.4362 | 10.4956 | 9.7743 | 9.7743 | 4.9698 | 0.035339 | 0.034133 | 0.059694 | 0.060572 | 1.7326
149 | - | - | 7 | 0.44163 | 38.02 | 34.635 | 10.5562 | 9.8349 | 9.8349 | 5.0039 | 0.034133 | 0.033006 | 0.060572 | 0.055704 | 1.7304
154 | - | - | 7 | 0.44163 | 38.02 | 34.8177 | 10.6119 | 9.8906 | 9.8906 | 5.037 | 0.033006 | 0.031952 | 0.055704 | 0.04288 | 1.5121
159 | - | - | 7 | 0.44163 | 38.02 | 34.9584 | 10.6548 | 9.9334 | 9.9334 | 5.0689 | 0.031952 | 0.030962 | 0.04288 | 0.060598 | 1.6544
164 | - | - | 7 | 0.44163 | 38.02 | 35.1572 | 10.7154 | 9.994 | 9.994 | 5.0999 | 0.030962 | 0.030032 | 0.060598 | 0.0555 | 1.9018
169 | - | - | 7 | 0.44163 | 38.02 | 35.3393 | 10.7709 | 10.0495 | 10.0495 | 5.1299 | 0.030032 | 0.029157 | 0.0555 | 0.049074 | 1.7644 | 0.21244 | 0.17512 | 0.34971 | 0.29029 | 1.6525
174 | - | - | 7 | 0.44163 | 38.02 | 35.5003 | 10.82 | 10.0986 | 10.0986 | 5.1591 | 0.029157 | 0.028331 | 0.049074 | 0.04808 | 1.6902
179 | - | - | 7 | 0.44163 | 38.02 | 35.6581 | 10.8681 | 10.1467 | 10.1467 | 5.1874 | 0.028331 | 0.02755 | 0.04808 | 0.0412 | 1.5949
184 | - | - | 7 | 0.44163 | 38.02 | 35.7933 | 10.9093 | 10.1879 | 10.1879 | 5.2149 | 0.02755 | 0.026811 | 0.0412 | 0.044796 | 1.5843
189 | - | - | 7 | 0.44163 | 38.02 | 35.9402 | 10.9541 | 10.2327 | 10.2327 | 5.2417 | 0.026811 | 0.026111 | 0.044796 | 0.05211 | 1.8354
194 | - | - | 7 | 0.44163 | 38.02 | 36.1112 | 11.0062 | 10.2848 | 10.2848 | 5.2679 | 0.026111 | 0.025447 | 0.05211 | 0.034976 | 1.6811
199 | - | - | 7 | 0.44163 | 38.02 | 36.226 | 11.0411 | 10.3198 | 10.3198 | 5.2933 | 0.025447 | 0.024815 | 0.034976 | 0.046192 | 1.621
204 | - | - | 7 | 0.44163 | 38.02 | 36.3775 | 11.0873 | 10.366 | 10.366 | 5.3181 | 0.024815 | 0.024214 | 0.046192 | 0.033282 | 1.615
209 | - | - | 7 | 0.44163 | 38.02 | 36.4867 | 11.1206 | 10.3992 | 10.3992 | 5.3423 | 0.024214 | 0.023642 | 0.033282 | 0.043296 | 1.6056 | 0.17512 | 0.14897 | 0.29029 | 0.22211 | 1.5676
214 | - | - | 7 | 0.44163 | 38.02 | 36.6288 | 11.1639 | 10.4425 | 10.4425 | 5.366 | 0.023642 | 0.023096 | 0.043296 | 0.040268 | 1.7869
219 | - | - | 7 | 0.44163 | 38.02 | 36.7609 | 11.2042 | 10.4828 | 10.4828 | 5.3891 | 0.023096 | 0.022574 | 0.040268 | 0.037998 | 1.713
224 | - | - | 7 | 0.44163 | 38.02 | 36.8856 | 11.2422 | 10.5208 | 10.5208 | 5.4116 | 0.022574 | 0.022076 | 0.037998 | 0.034284 | 1.6174
229 | - | - | 7 | 0.44163 | 38.02 | 36.9981 | 11.2765 | 10.5551 | 10.5551 | 5.4337 | 0.022076 | 0.021599 | 0.034284 | 0.035688 | 1.6032
234 | - | - | 7 | 0.44163 | 38.02 | 37.1152 | 11.3121 | 10.5908 | 10.5908 | 5.4553 | 0.021599 | 0.021142 | 0.035688 | 0.032788 | 1.601
239 | - | - | 7 | 0.44163 | 38.02 | 37.2227 | 11.3449 | 10.6236 | 10.6236 | 5.4765 | 0.021142 | 0.020705 | 0.032788 | 0.035084 | 1.6234
244 | - | - | 7 | 0.44163 | 38.02 | 37.3378 | 11.38 | 10.6587 | 10.6587 | 5.4972 | 0.020705 | 0.020285 | 0.035084 | 0.030882 | 1.6076
249 | - | - | 7 | 0.44163 | 38.02 | 37.4392 | 11.4109 | 10.6895 | 10.6895 | 5.5175 | 0.020285 | 0.019881 | 0.030882 | 0.027388 | 1.4493 | 0.14897 | 0.12963 | 0.22211 | 0.20618 | 1.5442
254 | - | - | 7 | 0.44163 | 38.02 | 37.529 | 11.4383 | 10.7169 | 10.7169 | 5.5373 | 0.019881 | 0.019494 | 0.027388 | 0.02689 | 1.3785
259 | - | - | 7 | 0.44163 | 38.02 | 37.6173 | 11.4652 | 10.7438 | 10.7438 | 5.5568 | 0.019494 | 0.019121 | 0.02689 | 0.038988 | 1.7124
264 | - | - | 7 | 0.44163 | 38.02 | 37.7452 | 11.5042 | 10.7828 | 10.7828 | 5.5759 | 0.019121 | 0.018762 | 0.038988 | 0.02868 | 1.7814
269 | - | - | 7 | 0.44163 | 38.02 | 37.8393 | 11.5328 | 10.8115 | 10.8115 | 5.5947 | 0.018762 | 0.018417 | 0.02868 | 0.029394 | 1.5626
274 | - | - | 7 | 0.44163 | 38.02 | 37.9357 | 11.5622 | 10.8409 | 10.8409 | 5.6131 | 0.018417 | 0.018084 | 0.029394 | 0.029488 | 1.6135
279 | - | - | 7 | 0.44163 | 38.02 | 38.0325 | 11.5917 | 10.8704 | 10.8704 | 5.6312 | 0.018084 | 0.017762 | 0.029488 | 0.022492 | 1.4468
284 | - | - | 7 | 0.44163 | 38.02 | 38.1063 | 11.6142 | 10.8929 | 10.8929 | 5.649 | 0.017762 | 0.017452 | 0.022492 | 0.018792 | 1.1707
289 | - | - | 7 | 0.44163 | 38.02 | 38.1679 | 11.633 | 10.9116 | 10.9116 | 5.6664 | 0.017452 | 0.017153 | 0.018792 | 0.037082 | 1.624 | 0.12963 | 0.11474 | 0.20618 | 0.19105 | 1.6301
294 | - | - | 7 | 0.44163 | 38.02 | 38.2896 | 11.6701 | 10.9487 | 10.9487 | 5.6836 | 0.017153 | 0.016864 | 0.037082 | 0.020402 | 1.6818
299 | - | - | 7 | 0.44163 | 38.02 | 38.3565 | 11.6905 | 10.9691 | 10.9691 | 5.7004 | 0.016864 | 0.016584 | 0.020402 | 0.028488 | 1.4659
304 | - | - | 7 | 0.44163 | 38.02 | 38.45 | 11.719 | 10.9976 | 10.9976 | 5.717 | 0.016584 | 0.016314 | 0.028488 | 0.022882 | 1.5589
309 | - | - | 7 | 0.44163 | 38.02 | 38.5251 | 11.7419 | 11.0205 | 11.0205 | 5.7333 | 0.016314 | 0.016052 | 0.022882 | 0.026782 | 1.5366
314 | - | - | 7 | 0.44163 | 38.02 | 38.613 | 11.7687 | 11.0473 | 11.0473 | 5.7494 | 0.016052 | 0.015798 | 0.026782 | 0.029178 | 1.7584
319 | - | - | 7 | 0.44163 | 38.02 | 38.7087 | 11.7978 | 11.0765 | 11.0765 | 5.7652 | 0.015798 | 0.015552 | 0.029178 | 0.02618 | 1.7645
324 | - | - | 7 | 0.44163 | 38.02 | 38.7946 | 11.824 | 11.1026 | 11.1026 | 5.7807 | 0.015552 | 0.015314 | 0.02618 | 0.015184 | 1.3348
329 | - | - | 7 | 0.44163 | 38.02 | 38.8444 | 11.8392 | 11.1178 | 11.1178 | 5.7961 | 0.015314 | 0.015083 | 0.015184 | 0.027084 | 1.3966 | 0.11474 | 0.10292 | 0.19105 | 0.16236 | 1.619
334 | - | - | 7 | 0.44163 | 38.02 | 38.9333 | 11.8663 | 11.1449 | 11.1449 | 5.8111 | 0.015083 | 0.014859 | 0.027084 | 0.02549 | 1.7553
339 | - | - | 7 | 0.44163 | 38.02 | 39.0169 | 11.8918 | 11.1704 | 11.1704 | 5.826 | 0.014859 | 0.014642 | 0.02549 | 0.022498 | 1.6254
344 | - | - | 7 | 0.44163 | 38.02 | 39.0907 | 11.9143 | 11.1929 | 11.1929 | 5.8406 | 0.014642 | 0.01443 | 0.022498 | 0.02051 | 1.4785
349 | - | - | 7 | 0.44163 | 38.02 | 39.158 | 11.9348 | 11.2134 | 11.2134 | 5.8551 | 0.01443 | 0.014225 | 0.02051 | 0.03118 | 1.8094
354 | - | - | 7 | 0.44163 | 38.02 | 39.2603 | 11.966 | 11.2446 | 11.2446 | 5.8693 | 0.014225 | 0.014025 | 0.03118 | 0.01409 | 1.5941
359 | - | - | 7 | 0.44163 | 38.02 | 39.3065 | 11.98 | 11.2587 | 11.2587 | 5.8833 | 0.014025 | 0.013831 | 0.01409 | 0.023314 | 1.3475
364 | - | - | 7 | 0.44163 | 38.02 | 39.383 | 12.0034 | 11.282 | 11.282 | 5.8972 | 0.013831 | 0.013643 | 0.023314 | 0.026886 | 1.8291
369 | - | - | 7 | 0.44163 | 38.02 | 39.4712 | 12.0302 | 11.3089 | 11.3089 | 5.9108 | 0.013643 | 0.013459 | 0.026886 | 0.015586 | 1.5616 | 0.10292 | 0.093308 | 0.16236 | 0.15367 | 1.6139
374 | - | - | 7 | 0.44163 | 38.02 | 39.5224 | 12.0458 | 11.3245 | 11.3245 | 5.9243 | 0.013459 | 0.01328 | 0.015586 | 0.028196 | 1.6438
379 | - | - | 7 | 0.44163 | 38.02 | 39.6149 | 12.074 | 11.3527 | 11.3527 | 5.9375 | 0.01328 | 0.013106 | 0.028196 | 0.021308 | 1.8728
384 | - | - | 7 | 0.44163 | 38.02 | 39.6848 | 12.0953 | 11.374 | 11.374 | 5.9506 | 0.013106 | 0.012937 | 0.021308 | 0.028786 | 1.9274
389 | - | - | 7 | 0.44163 | 38.02 | 39.7793 | 12.1241 | 11.4028 | 11.4028 | 5.9636 | 0.012937 | 0.012772 | 0.028786 | 0.010482 | 1.5184
394 | - | - | 7 | 0.44163 | 38.02 | 39.8136 | 12.1346 | 11.4132 | 11.4132 | 5.9764 | 0.012772 | 0.012611 | 0.010482 | 0.016188 | 1.0537
399 | - | - | 7 | 0.44163 | 38.02 | 39.8668 | 12.1508 | 11.4294 | 11.4294 | 5.989 | 0.012611 | 0.012453 | 0.016188 | 0.021194 | 1.4941
404 | - | - | 7 | 0.44163 | 38.02 | 39.9363 | 12.172 | 11.4506 | 11.4506 | 6.0014 | 0.012453 | 0.0123 | 0.021194 | 0.020622 | 1.6891
409 | - | - | 7 | 0.44163 | 38.02 | 40.004 | 12.1926 | 11.4712 | 11.4712 | 6.0137 | 0.0123 | 0.012151 | 0.020622 | 0.022076 | 1.7471 | 0.093308 | 0.08534 | 0.15367 | 0.14181 | 1.6546
414 | - | - | 7 | 0.44163 | 38.02 | 40.0764 | 12.2147 | 11.4933 | 11.4933 | 6.0259 | 0.012151 | 0.012005 | 0.022076 | 0.01289 | 1.4431
419 | - | - | 7 | 0.44163 | 38.02 | 40.1187 | 12.2276 | 11.5062 | 11.5062 | 6.0379 | 0.012005 | 0.011863 | 0.01289 | 0.026898 | 1.6742
424 | - | - | 7 | 0.44163 | 38.02 | 40.2069 | 12.2545 | 11.5331 | 11.5331 | 6.0497 | 0.011863 | 0.011723 | 0.026898 | 0.019294 | 1.9548
429 | - | - | 7 | 0.44163 | 38.02 | 40.2702 | 12.2738 | 11.5524 | 11.5524 | 6.0615 | 0.011723 | 0.011588 | 0.019294 | 0.014112 | 1.4306
434 | - | - | 7 | 0.44163 | 38.02 | 40.3165 | 12.2879 | 11.5665 | 11.5665 | 6.073 | 0.011588 | 0.011455 | 0.014112 | 0.023202 | 1.624
439 | - | - | 7 | 0.44163 | 38.02 | 40.3927 | 12.3111 | 11.5897 | 11.5897 | 6.0845 | 0.011455 | 0.011325 | 0.023202 | 0.018786 | 1.8411
444 | - | - | 7 | 0.44163 | 38.02 | 40.4543 | 12.3299 | 11.6085 | 11.6085 | 6.0958 | 0.011325 | 0.011198 | 0.018786 | 0.01641 | 1.5615
449 | - | - | 7 | 0.44163 | 38.02 | 40.5081 | 12.3463 | 11.6249 | 11.6249 | 6.107 | 0.011198 | 0.011074 | 0.01641 | 0.02289 | 1.7678 | 0.08534 | 0.078626 | 0.14181 | 0.12229 | 1.6064
454 | - | - | 7 | 0.44163 | 38.02 | 40.5832 | 12.3692 | 11.6478 | 11.6478 | 6.1181 | 0.011074 | 0.010953 | 0.02289 | 0.013798 | 1.6611
459 | - | - | 7 | 0.44163 | 38.02 | 40.6285 | 12.383 | 11.6616 | 11.6616 | 6.1291 | 0.010953 | 0.010834 | 0.013798 | 0.015878 | 1.3632
464 | - | - | 7 | 0.44163 | 38.02 | 40.6806 | 12.3988 | 11.6775 | 11.6775 | 6.1399 | 0.010834 | 0.010718 | 0.015878 | 0.019902 | 1.6622
469 | - | - | 7 | 0.44163 | 38.02 | 40.7459 | 12.4187 | 11.6974 | 11.6974 | 6.1506 | 0.010718 | 0.010605 | 0.019902 | 0.017408 | 1.7486
474 | - | - | 7 | 0.44163 | 38.02 | 40.803 | 12.4362 | 11.7148 | 11.7148 | 6.1612 | 0.010605 | 0.010493 | 0.017408 | 0.017218 | 1.6412
479 | - | - | 7 | 0.44163 | 38.02 | 40.8595 | 12.4534 | 11.732 | 11.732 | 6.1717 | 0.010493 | 0.010384 | 0.017218 | 0.01901 | 1.7362
484 | - | - | 7 | 0.44163 | 38.02 | 40.9219 | 12.4724 | 11.751 | 11.751 | 6.1821 | 0.010384 | 0.010278 | 0.01901 | 0.015704 | 1.6785
489 | - | - | 7 | 0.44163 | 38.02 | 40.9734 | 12.4881 | 11.7667 | 11.7667 | 6.1924 | 0.010278 | 0.010173 | 0.015704 | 0.0095059 | 1.2297 | 0.078626 | 0.072892 | 0.12229 | 0.12486 | 1.6371
494 | - | - | 7 | 0.44163 | 38.02 | 41.0046 | 12.4976 | 11.7762 | 11.7762 | 6.2025 | 0.010173 | 0.010071 | 0.0095059 | 0.024102 | 1.6676
499 | - | - | 7 | 0.44163 | 38.02 | 41.0837 | 12.5217 | 11.8003 | 11.8003 | 6.2126 | 0.010071 | 0.0099702 | 0.024102 | 0.018088 | 2.1023
504 | - | - | 7 | 0.44163 | 38.02 | 41.143 | 12.5398 | 11.8184 | 11.8184 | 6.2226 | 0.0099702 | 0.0098717 | 0.018088 | 0.013998 | 1.6151
509 | - | - | 7 | 0.44163 | 38.02 | 41.189 | 12.5538 | 11.8324 | 11.8324 | 6.2324 | 0.0098717 | 0.0097752 | 0.013998 | 0.011302 | 1.2864
514 | - | - | 7 | 0.44163 | 38.02 | 41.226 | 12.5651 | 11.8437 | 11.8437 | 6.2422 | 0.0097752 | 0.0096806 | 0.011302 | 0.0167 | 1.442
519 | - | - | 7 | 0.44163 | 38.02 | 41.2808 | 12.5818 | 11.8604 | 11.8604 | 6.2519 | 0.0096806 | 0.0095878 | 0.0167 | 0.016404 | 1.718
524 | - | - | 7 | 0.44163 | 38.02 | 41.3347 | 12.5982 | 11.8768 | 11.8768 | 6.2615 | 0.0095878 | 0.0094967 | 0.016404 | 0.012194 | 1.4965
529 | - | - | 7 | 0.44163 | 38.02 | 41.3747 | 12.6104 | 11.889 | 11.889 | 6.271 | 0.0094967 | 0.0094074 | 0.012194 | 0.020402 | 1.7285 | 0.072892 | 0.067938 | 0.12486 | 0.12778 | 1.7998
534 | - | - | 7 | 0.44163 | 38.02 | 41.4416 | 12.6308 | 11.9094 | 11.9094 | 6.2804 | 0.0094074 | 0.0093197 | 0.020402 | 0.018608 | 2.0823
539 | - | - | 7 | 0.44163 | 38.02 | 41.5027 | 12.6494 | 11.928 | 11.928 | 6.2897 | 0.0093197 | 0.0092337 | 0.018608 | 0.016508 | 1.8917
544 | - | - | 7 | 0.44163 | 38.02 | 41.5568 | 12.6659 | 11.9445 | 11.9445 | 6.2989 | 0.0092337 | 0.0091492 | 0.016508 | 0.021008 | 2.0431
549 | - | - | 7 | 0.44163 | 38.02 | 41.6257 | 12.6869 | 11.9655 | 11.9655 | 6.3081 | 0.0091492 | 0.0090662 | 0.021008 | 0.0067079 | 1.5145
554 | - | - | 7 | 0.44163 | 38.02 | 41.6478 | 12.6936 | 11.9722 | 11.9722 | 6.3172 | 0.0090662 | 0.0089848 | 0.0067079 | 0.018902 | 1.4249
559 | - | - | 7 | 0.44163 | 38.02 | 41.7098 | 12.7125 | 11.9911 | 11.9911 | 6.3261 | 0.0089848 | 0.0089048 | 0.018902 | 0.017118 | 2.0126
564 | - | - | 7 | 0.44163 | 38.02 | 41.7659 | 12.7296 | 12.0083 | 12.0083 | 6.3351 | 0.0089048 | 0.0088262 | 0.017118 | 0.0056059 | 1.2759
569 | - | - | 7 | 0.44163 | 38.02 | 41.7843 | 12.7352 | 12.0139 | 12.0139 | 6.3439 | 0.0088262 | 0.008749 | 0.0056059 | 0.017398 | 1.3148 | 0.067938 | 0.063614 | 0.12778 | 0.10522 | 1.7637
574 | - | - | 7 | 0.44163 | 38.02 | 41.8414 | 12.7526 | 12.0313 | 12.0313 | 6.3526 | 0.008749 | 0.0086731 | 0.017398 | 0.012712 | 1.726
579 | - | - | 7 | 0.44163 | 38.02 | 41.8831 | 12.7654 | 12.044 | 12.044 | 6.3613 | 0.0086731 | 0.0085985 | 0.012712 | 0.01801 | 1.7815
584 | - | - | 7 | 0.44163 | 38.02 | 41.9422 | 12.7834 | 12.062 | 12.062 | 6.3699 | 0.0085985 | 0.0085252 | 0.01801 | 0.013214 | 1.8211
589 | - | - | 7 | 0.44163 | 38.02 | 41.9856 | 12.7966 | 12.0752 | 12.0752 | 6.3784 | 0.0085252 | 0.0084531 | 0.013214 | 0.012506 | 1.5146
594 | - | - | 7 | 0.44163 | 38.02 | 42.0266 | 12.8091 | 12.0877 | 12.0877 | 6.3869 | 0.0084531 | 0.0083823 | 0.012506 | 0.017426 | 1.7804
599 | - | - | 7 | 0.44163 | 38.02 | 42.0838 | 12.8265 | 12.1051 | 12.1051 | 6.3953 | 0.0083823 | 0.0083126 | 0.017426 | 0.017406 | 2.0864
604 | - | - | 7 | 0.44163 | 38.02 | 42.1409 | 12.8439 | 12.1225 | 12.1225 | 6.4036 | 0.0083126 | 0.0082441 | 0.017406 | 0.01911 | 2.2064
609 | - | - | 7 | 0.44163 | 38.02 | 42.2036 | 12.863 | 12.1417 | 12.1417 | 6.4118 | 0.0082441 | 0.0081767 | 0.01911 | 0.010608 | 1.8056 | 0.063614 | 0.059809 | 0.10522 | 0.08618 | 1.5442
614 | - | - | 7 | 0.44163 | 38.02 | 42.2384 | 12.8736 | 12.1523 | 12.1523 | 6.42 | 0.0081767 | 0.0081103 | 0.010608 | 0.01701 | 1.699
619 | - | - | 7 | 0.44163 | 38.02 | 42.2942 | 12.8906 | 12.1693 | 12.1693 | 6.4281 | 0.0081103 | 0.0080451 | 0.01701 | 0.0073 | 1.4999
624 | - | - | 7 | 0.44163 | 38.02 | 42.3181 | 12.8979 | 12.1766 | 12.1766 | 6.4362 | 0.0080451 | 0.0079809 | 0.0073 | 0.01621 | 1.4715
629 | - | - | 7 | 0.44163 | 38.02 | 42.3713 | 12.9141 | 12.1928 | 12.1928 | 6.4441 | 0.0079809 | 0.0079177 | 0.01621 | 0.007196 | 1.4677
634 | - | - | 7 | 0.44163 | 38.02 | 42.3949 | 12.9213 | 12.2 | 12.2 | 6.452 | 0.0079177 | 0.0078555 | 0.007196 | 0.019792 | 1.7174
639 | - | - | 7 | 0.44163 | 38.02 | 42.4599 | 12.9411 | 12.2198 | 12.2198 | 6.4599 | 0.0078555 | 0.0077943 | 0.019792 | 0.011706 | 2.0087
644 | - | - | 7 | 0.44163 | 38.02 | 42.4983 | 12.9528 | 12.2315 | 12.2315 | 6.4677 | 0.0077943 | 0.007734 | 0.011706 | 0.015398 | 1.7474
649 | - | - | 7 | 0.44163 | 38.02 | 42.5488 | 12.9682 | 12.2469 | 12.2469 | 6.4754 | 0.007734 | 0.0076746 | 0.015398 | 0.01121 | 1.7248 | 0.059809 | 0.056432 | 0.08618 | 0.10118 | 1.6221
654 | - | - | 7 | 0.44163 | 38.02 | 42.5856 | 12.9795 | 12.2581 | 12.2581 | 6.4831 | 0.0076746 | 0.0076162 | 0.01121 | 0.010608 | 1.4266
659 | - | - | 7 | 0.44163 | 38.02 | 42.6204 | 12.9901 | 12.2687 | 12.2687 | 6.4907 | 0.0076162 | 0.0075586 | 0.010608 | 0.0138 | 1.6101
664 | - | - | 7 | 0.44163 | 38.02 | 42.6657 | 13.0039 | 12.2825 | 12.2825 | 6.4983 | 0.0075586 | 0.0075019 | 0.0138 | 0.0072921 | 1.3973
669 | - | - | 7 | 0.44163 | 38.02 | 42.6896 | 13.0112 | 12.2898 | 12.2898 | 6.5058 | 0.0075019 | 0.0074461 | 0.0072921 | 0.010812 | 1.2129
674 | - | - | 7 | 0.44163 | 38.02 | 42.7251 | 13.022 | 12.3006 | 12.3006 | 6.5132 | 0.0074461 | 0.007391 | 0.010812 | 0.0081783 | 1.2786
679 | - | - | 7 | 0.44163 | 38.02 | 42.7519 | 13.0301 | 12.3088 | 12.3088 | 6.5206 | 0.007391 | 0.0073368 | 0.0081783 | 0.013988 | 1.508
684 | - | - | 7 | 0.44163 | 38.02 | 42.7978 | 13.0441 | 12.3228 | 12.3228 | 6.528 | 0.0073368 | 0.0072834 | 0.013988 | 0.010292 | 1.6589
689 | - | - | 7 | 0.44163 | 38.02 | 42.8316 | 13.0544 | 12.3331 | 12.3331 | 6.5352 | 0.0072834 | 0.0072307 | 0.010292 | 0.013692 | 1.6542 | 0.056432 | 0.053417 | 0.10118 | 0.086374 | 1.7026
694 | - | - | 7 | 0.44163 | 38.02 | 42.8765 | 13.0681 | 12.3467 | 12.3467 | 6.5425 | 0.0072307 | 0.0071788 | 0.013692 | 0.016008 | 2.0624
699 | - | - | 7 | 0.44163 | 38.02 | 42.929 | 13.0841 | 12.3628 | 12.3628 | 6.5497 | 0.0071788 | 0.0071276 | 0.016008 | 0.0131 | 2.0332
704 | - | - | 7 | 0.44163 | 38.02 | 42.972 | 13.0972 | 12.3759 | 12.3759 | 6.5568 | 0.0071276 | 0.0070772 | 0.0131 | 0.009298 | 1.5749
709 | - | - | 7 | 0.44163 | 38.02 | 43.0025 | 13.1065 | 12.3851 | 12.3851 | 6.5639 | 0.0070772 | 0.0070274 | 0.009298 | 0.010096 | 1.3755
714 | - | - | 7 | 0.44163 | 38.02 | 43.0356 | 13.1166 | 12.3952 | 12.3952 | 6.5709 | 0.0070274 | 0.0069784 | 0.010096 | 0.01621 | 1.8813
719 | - | - | 7 | 0.44163 | 38.02 | 43.0888 | 13.1328 | 12.4115 | 12.4115 | 6.5779 | 0.0069784 | 0.00693 | 0.01621 | 0.0073901 | 1.6924
724 | - | - | 7 | 0.44163 | 38.02 | 43.113 | 13.1402 | 12.4188 | 12.4188 | 6.5848 | 0.00693 | 0.0068823 | 0.0073901 | 0.01539 | 1.6533
729 | - | - | 7 | 0.44163 | 38.02 | 43.1635 | 13.1556 | 12.4342 | 12.4342 | 6.5917 | 0.0068823 | 0.0068353 | 0.01539 | 0.0179 | 2.4281 | 0.053417 | 0.050708 | 0.086374 | 0.079668 | 1.5935
734 | - | - | 7 | 0.44163 | 38.02 | 43.2223 | 13.1735 | 12.4521 | 12.4521 | 6.5985 | 0.0068353 | 0.0067889 | 0.0179 | 0.001596 | 1.4229
739 | - | - | 7 | 0.44163 | 38.02 | 43.2275 | 13.1751 | 12.4537 | 12.4537 | 6.6053 | 0.0067889 | 0.0067431 | 0.001596 | 0.0061901 | 0.5777
744 | - | - | 7 | 0.44163 | 38.02 | 43.2478 | 13.1813 | 12.4599 | 12.4599 | 6.612 | 0.0067431 | 0.0066979 | 0.0061901 | 0.020788 | 2.0145
749 | - | - | 7 | 0.44163 | 38.02 | 43.316 | 13.2021 | 12.4807 | 12.4807 | 6.6187 | 0.0066979 | 0.0066534 | 0.020788 | 0.0095822 | 2.2692
754 | - | - | 7 | 0.44163 | 38.02 | 43.3475 | 13.2117 | 12.4903 | 12.4903 | 6.6254 | 0.0066534 | 0.0066094 | 0.0095822 | 0.011706 | 1.6062
759 | - | - | 7 | 0.44163 | 38.02 | 43.3859 | 13.2234 | 12.502 | 12.502 | 6.632 | 0.0066094 | 0.006566 | 0.011706 | 0.010202 | 1.6621
764 | - | - | 7 | 0.44163 | 38.02 | 43.4193 | 13.2336 | 12.5122 | 12.5122 | 6.6386 | 0.006566 | 0.0065232 | 0.010202 | 0.0084099 | 1.4211
769 | - | - | 7 | 0.44163 | 38.02 | 43.4469 | 13.242 | 12.5206 | 12.5206 | 6.6451 | 0.0065232 | 0.0064809 | 0.0084099 | 0.013976 | 1.7243 | 0.050708 | 0.04826 | 0.079668 | 0.07731 | 1.5869
774 | - | - | 7 | 0.44163 | 38.02 | 43.4928 | 13.256 | 12.5346 | 12.5346 | 6.6516 | 0.0064809 | 0.0064392 | 0.013976 | 0.008498 | 1.7368
779 | - | - | 7 | 0.44163 | 38.02 | 43.5207 | 13.2645 | 12.5431 | 12.5431 | 6.658 | 0.0064392 | 0.006398 | 0.008498 | 0.0055138 | 1.09
784 | - | - | 7 | 0.44163 | 38.02 | 43.5388 | 13.27 | 12.5486 | 12.5486 | 6.6644 | 0.006398 | 0.0063573 | 0.0055138 | 0.015094 | 1.6205
789 | - | - | 7 | 0.44163 | 38.02 | 43.5883 | 13.2851 | 12.5637 | 12.5637 | 6.6708 | 0.0063573 | 0.0063171 | 0.015094 | 0.010796 | 2.0406
794 | - | - | 7 | 0.44163 | 38.02 | 43.6237 | 13.2959 | 12.5745 | 12.5745 | 6.6771 | 0.0063171 | 0.0062775 | 0.010796 | 0.0061138 | 1.3403
799 | - | - | 7 | 0.44163 | 38.02 | 43.6438 | 13.302 | 12.5806 | 12.5806 | 6.6834 | 0.0062775 | 0.0062383 | 0.0061138 | 0.0057901 | 0.95097
804 | - | - | 7 | 0.44163 | 38.02 | 43.6628 | 13.3078 | 12.5864 | 12.5864 | 6.6896 | 0.0062383 | 0.0061996 | 0.0057901 | 0.013886 | 1.586
809 | - | - | 7 | 0.44163 | 38.02 | 43.7083 | 13.3216 | 12.6003 | 12.6003 | 6.6958 | 0.0061996 | 0.0061614 | 0.013886 | 0.0051079 | 1.5322 | 0.04826 | 0.046038 | 0.07731 | 0.070982 | 1.5712
814 | - | - | 7 | 0.44163 | 38.02 | 43.7251 | 13.3268 | 12.6054 | 12.6054 | 6.702 | 0.0061614 | 0.0061237 | 0.0051079 | 0.016194 | 1.7395
819 | - | - | 7 | 0.44163 | 38.02 | 43.7782 | 13.343 | 12.6216 | 12.6216 | 6.7081 | 0.0061237 | 0.0060864 | 0.016194 | 0.014494 | 2.5125
824 | - | - | 7 | 0.44163 | 38.02 | 43.8258 | 13.3574 | 12.6361 | 12.6361 | 6.7142 | 0.0060864 | 0.0060496 | 0.014494 | 0.0058039 | 1.6682
829 | - | - | 7 | 0.44163 | 38.02 | 43.8448 | 13.3632 | 12.6419 | 12.6419 | 6.7202 | 0.0060496 | 0.0060132 | 0.0058039 | 0.0082941 | 1.17
834 | - | - | 7 | 0.44163 | 38.02 | 43.872 | 13.3715 | 12.6502 | 12.6502 | 6.7262 | 0.0060132 | 0.0059773 | 0.0082941 | 0.008402 | 1.3925
839 | - | - | 7 | 0.44163 | 38.02 | 43.8996 | 13.3799 | 12.6586 | 12.6586 | 6.7322 | 0.0059773 | 0.0059418 | 0.008402 | 0.0085059 | 1.4186
844 | - | - | 7 | 0.44163 | 38.02 | 43.9275 | 13.3885 | 12.6671 | 12.6671 | 6.7382 | 0.0059418 | 0.0059067 | 0.0085059 | 0.010508 | 1.6058
849 | - | - | 7 | 0.44163 | 38.02 | 43.962 | 13.399 | 12.6776 | 12.6776 | 6.7441 | 0.0059067 | 0.005872 | 0.010508 | 0.011486 | 1.8678 | 0.046038 | 0.044012 | 0.070982 | 0.089114 | 1.7887
854 | - | - | 7 | 0.44163 | 38.02 | 43.9997 | 13.4104 | 12.6891 | 12.6891 | 6.7499 | 0.005872 | 0.0058377 | 0.011486 | 0.0073099 | 1.6031
859 | - | - | 7 | 0.44163 | 38.02 | 44.0237 | 13.4178 | 12.6964 | 12.6964 | 6.7558 | 0.0058377 | 0.0058038 | 0.0073099 | 0.00040592 | 0.65934
864 | - | - | 7 | 0.44163 | 38.02 | 44.025 | 13.4182 | 12.6968 | 12.6968 | 6.7616 | 0.0058038 | 0.0057704 | 0.00040592 | 0.017498 | 1.5555
869 | - | - | 7 | 0.44163 | 38.02 | 44.0824 | 13.4357 | 12.7143 | 12.7143 | 6.7673 | 0.0057704 | 0.0057373 | 0.017498 | 0.0133 | 2.6743
874 | - | - | 7 | 0.44163 | 38.02 | 44.126 | 13.449 | 12.7276 | 12.7276 | 6.7731 | 0.0057373 | 0.0057045 | 0.0133 | -0.001402 | 1.0325
879 | - | - | 7 | 0.44163 | 38.02 | 44.1214 | 13.4476 | 12.7262 | 12.7262 | 6.7788 | 0.0057045 | 0.0056722 | -0.001402 | 0.018786 | 1.5382
884 | - | - | 7 | 0.44163 | 38.02 | 44.1831 | 13.4663 | 12.745 | 12.745 | 6.7845 | 0.0056722 | 0.0056402 | 0.018786 | 0.003598 | 1.9712
889 | - | - | 7 | 0.44163 | 38.02 | 44.1949 | 13.4699 | 12.7486 | 12.7486 | 6.7901 | 0.0056402 | 0.0056085 | 0.003598 | 0.0069118 | 0.93599 | 0.044012 | 0.042156 | 0.089114 | 0.077637 | 1.9313
894 | - | - | 7 | 0.44163 | 38.02 | 44.2176 | 13.4769 | 12.7555 | 12.7555 | 6.7957 | 0.0056085 | 0.0055773 | 0.0069118 | 0.015994 | 2.0523
899 | - | - | 7 | 0.44163 | 38.02 | 44.27 | 13.4928 | 12.7715 | 12.7715 | 6.8013 | 0.0055773 | 0.0055463 | 0.015994 | 0.0067119 | 2.0366
904 | - | - | 7 | 0.44163 | 38.02 | 44.2921 | 13.4996 | 12.7782 | 12.7782 | 6.8068 | 0.0055463 | 0.0055157 | 0.0067119 | 0.016686 | 2.1202
909 | - | - | 7 | 0.44163 | 38.02 | 44.3468 | 13.5162 | 12.7949 | 12.7949 | 6.8123 | 0.0055157 | 0.0054855 | 0.016686 | 0.015196 | 2.8974
914 | - | - | 7 | 0.44163 | 38.02 | 44.3967 | 13.5314 | 12.8101 | 12.8101 | 6.8178 | 0.0054855 | 0.0054556 | 0.015196 | 0.011912 | 2.476
919 | - | - | 7 | 0.44163 | 38.02 | 44.4357 | 13.5434 | 12.822 | 12.822 | 6.8233 | 0.0054556 | 0.0054259 | 0.011912 | 0.0075099 | 1.7827
924 | - | - | 7 | 0.44163 | 38.02 | 44.4604 | 13.5509 | 12.8295 | 12.8295 | 6.8287 | 0.0054259 | 0.0053967 | 0.0075099 | 0.0081921 | 1.4512
929 | - | - | 7 | 0.44163 | 38.02 | 44.4873 | 13.5591 | 12.8377 | 12.8377 | 6.8341 | 0.0053967 | 0.0053677 | 0.0081921 | 0.010004 | 1.6913 | 0.042156 | 0.04045 | 0.077637 | 0.06307 | 1.6975
934 | - | - | 7 | 0.44163 | 38.02 | 44.5201 | 13.5691 | 12.8477 | 12.8477 | 6.8395 | 0.0053677 | 0.005339 | 0.010004 | 0.0059079 | 1.4841
939 | - | - | 7 | 0.44163 | 38.02 | 44.5395 | 13.575 | 12.8536 | 12.8536 | 6.8448 | 0.005339 | 0.0053107 | 0.0059079 | 0.012 | 1.6846
944 | - | - | 7 | 0.44163 | 38.02 | 44.5788 | 13.587 | 12.8656 | 12.8656 | 6.8501 | 0.0053107 | 0.0052826 | 0.012 | 0.013908 | 2.4467
949 | - | - | 7 | 0.44163 | 38.02 | 44.6245 | 13.6009 | 12.8795 | 12.8795 | 6.8554 | 0.0052826 | 0.0052549 | 0.013908 | 0.0077079 | 2.0482
954 | - | - | 7 | 0.44163 | 38.02 | 44.6498 | 13.6086 | 12.8872 | 12.8872 | 6.8607 | 0.0052549 | 0.0052274 | 0.0077079 | 0.004798 | 1.1916
959 | - | - | 7 | 0.44163 | 38.02 | 44.6655 | 13.6134 | 12.892 | 12.892 | 6.8659 | 0.0052274 | 0.0052002 | 0.004798 | 0.0082118 | 1.2494
964 | - | - | 7 | 0.44163 | 38.02 | 44.6924 | 13.6216 | 12.9002 | 12.9002 | 6.8711 | 0.0052002 | 0.0051733 | 0.0082118 | 0.0151 | 2.2507
969 | - | - | 7 | 0.44163 | 38.02 | 44.742 | 13.6367 | 12.9153 | 12.9153 | 6.8763 | 0.0051733 | 0.0051467 | 0.0151 | -1.97e-06 | 1.4555 | 0.04045 | 0.038878 | 0.06307 | 0.057292 | 1.5156
974 | - | - | 7 | 0.44163 | 38.02 | 44.742 | 13.6367 | 12.9153 | 12.9153 | 6.8814 | 0.0051467 | 0.0051203 | -1.97e-06 | 0.0088901 | 0.87016
979 | - | - | 7 | 0.44163 | 38.02 | 44.7711 | 13.6456 | 12.9242 | 12.9242 | 6.8865 | 0.0051203 | 0.0050943 | 0.0088901 | 0.012 | 2.0467
984 | - | - | 7 | 0.44163 | 38.02 | 44.8105 | 13.6576 | 12.9362 | 12.9362 | 6.8916 | 0.0050943 | 0.0050684 | 0.012 | 0.014484 | 2.6073
989 | - | - | 7 | 0.44163 | 38.02 | 44.858 | 13.6721 | 12.9507 | 12.9507 | 6.8967 | 0.0050684 | 0.0050429 | 0.014484 | 0.0054 | 1.962
994 | - | - | 7 | 0.44163 | 38.02 | 44.8758 | 13.6775 | 12.9561 | 12.9561 | 6.9017 | 0.0050429 | 0.0050176 | 0.0054 | 0.0082079 | 1.354
999 | - | - | 7 | 0.44163 | 38.02 | 44.9027 | 13.6857 | 12.9643 | 12.9643 | 6.9068 | 0.0050176 | 0.0049925 | 0.0082079 | 0.0039961 | 1.2171
1004 | - | - | 7 | 0.44163 | 38.02 | 44.9158 | 13.6897 | 12.9683 | 12.9683 | 6.9117 | 0.0049925 | 0.0049677 | 0.0039961 | 0.010094 | 1.4177
1009 | - | - | 7 | 0.44163 | 38.02 | 44.9489 | 13.6998 | 12.9784 | 12.9784 | 6.9167 | 0.0049677 | 0.0049432 | 0.010094 | 0.0082961 | 1.8547 | 0.038878 | 0.037423 | 0.057292 | 0.06458 | 1.6021
1014 | - | - | 7 | 0.44163 | 38.02 | 44.9761 | 13.7081 | 12.9867 | 12.9867 | 6.9217 | 0.0049432 | 0.0049188 | 0.0082961 | 0.012198 | 2.0801
1019 | - | - | 7 | 0.44163 | 38.02 | 45.0162 | 13.7203 | 12.9989 | 12.9989 | 6.9266 | 0.0049188 | 0.0048948 | 0.012198 | 0.0057099 | 1.8216
1024 | - | - | 7 | 0.44163 | 38.02 | 45.0349 | 13.726 | 13.0046 | 13.0046 | 6.9315 | 0.0048948 | 0.0048709 | 0.0057099 | 0.0038901 | 0.98213
1029 | - | - | 7 | 0.44163 | 38.02 | 45.0477 | 13.7299 | 13.0085 | 13.0085 | 6.9363 | 0.0048709 | 0.0048473 | 0.0038901 | 0.012102 | 1.6497
1034 | - | - | 7 | 0.44163 | 38.02 | 45.0874 | 13.742 | 13.0206 | 13.0206 | 6.9412 | 0.0048473 | 0.0048239 | 0.012102 | 0.0132 | 2.6168
1039 | - | - | 7 | 0.44163 | 38.02 | 45.1307 | 13.7552 | 13.0338 | 13.0338 | 6.946 | 0.0048239 | 0.0048008 | 0.0132 | -0.003104 | 1.0408
1044 | - | - | 7 | 0.44163 | 38.02 | 45.1205 | 13.7521 | 13.0307 | 13.0307 | 6.9508 | 0.0048008 | 0.0047778 | -0.003104 | 0.005 | 0.202
1049 | - | - | 7 | 0.44163 | 38.02 | 45.1369 | 13.7571 | 13.0357 | 13.0357 | 6.9556 | 0.0047778 | 0.0047551 | 0.005 | 0.011204 | 1.7029 | 0.037423 | 0.036072 | 0.06458 | 0.063202 | 1.7391
1054 | - | - | 7 | 0.44163 | 38.02 | 45.1737 | 13.7683 | 13.0469 | 13.0469 | 6.9603 | 0.0047551 | 0.0047326 | 0.011204 | 0.0054881 | 1.7565
1059 | - | - | 7 | 0.44163 | 38.02 | 45.1917 | 13.7737 | 13.0524 | 13.0524 | 6.9651 | 0.0047326 | 0.0047103 | 0.0054881 | 0.0041178 | 1.0166
1064 | - | - | 7 | 0.44163 | 38.02 | 45.2052 | 13.7779 | 13.0565 | 13.0565 | 6.9698 | 0.0047103 | 0.0046882 | 0.0041178 | 0.015582 | 2.1018
1069 | - | - | 7 | 0.44163 | 38.02 | 45.2563 | 13.7934 | 13.0721 | 13.0721 | 6.9745 | 0.0046882 | 0.0046664 | 0.015582 | 0.0059961 | 2.3019
1074 | - | - | 7 | 0.44163 | 38.02 | 45.276 | 13.7994 | 13.0781 | 13.0781 | 6.9791 | 0.0046664 | 0.0046447 | 0.0059961 | 0.0053921 | 1.2228
1079 | - | - | 7 | 0.44163 | 38.02 | 45.2937 | 13.8048 | 13.0835 | 13.0835 | 6.9838 | 0.0046447 | 0.0046232 | 0.0053921 | 0.003 | 0.90432
1084 | - | - | 7 | 0.44163 | 38.02 | 45.3035 | 13.8078 | 13.0865 | 13.0865 | 6.9884 | 0.0046232 | 0.0046019 | 0.003 | 0.0138 | 1.8265
1089 | - | - | 7 | 0.44163 | 38.02 | 45.3488 | 13.8216 | 13.1003 | 13.1003 | 6.993 | 0.0046019 | 0.0045809 | 0.0138 | 0.007202 | 2.2838 | 0.036072 | 0.034816 | 0.063202 | 0.061076 | 1.7532
1094 | - | - | 7 | 0.44163 | 38.02 | 45.3724 | 13.8288 | 13.1075 | 13.1075 | 6.9976 | 0.0045809 | 0.00456 | 0.007202 | 0.010784 | 1.9695
1099 | - | - | 7 | 0.44163 | 38.02 | 45.4078 | 13.8396 | 13.1183 | 13.1183 | 7.0022 | 0.00456 | 0.0045393 | 0.010784 | 0.0030158 | 1.5127
1104 | - | - | 7 | 0.44163 | 38.02 | 45.4177 | 13.8426 | 13.1213 | 13.1213 | 7.0067 | 0.0045393 | 0.0045188 | 0.0030158 | 0.0086901 | 1.2952
1109 | - | - | 7 | 0.44163 | 38.02 | 45.4462 | 13.8513 | 13.13 | 13.13 | 7.0112 | 0.0045188 | 0.0044984 | 0.0086901 | 0.0075079 | 1.7958
1114 | - | - | 7 | 0.44163 | 38.02 | 45.4708 | 13.8588 | 13.1375 | 13.1375 | 7.0157 | 0.0044984 | 0.0044783 | 0.0075079 | 0.008804 | 1.8178
1119 | - | - | 7 | 0.44163 | 38.02 | 45.4997 | 13.8676 | 13.1463 | 13.1463 | 7.0202 | 0.0044783 | 0.0044583 | 0.008804 | 0.016096 | 2.79
1124 | - | - | 7 | 0.44163 | 38.02 | 45.5525 | 13.8837 | 13.1624 | 13.1624 | 7.0246 | 0.0044583 | 0.0044385 | 0.016096 | 0.001102 | 1.9256
1129 | - | - | 7 | 0.44163 | 38.02 | 45.5561 | 13.8848 | 13.1635 | 13.1635 | 7.0291 | 0.0044385 | 0.0044189 | 0.001102 | 0.006898 | 0.9061 | 0.034816 | 0.033645 | 0.061076 | 0.058234 | 1.7423
1134 | - | - | 7 | 0.44163 | 38.02 | 45.5788 | 13.8917 | 13.1704 | 13.1704 | 7.0335 | 0.0044189 | 0.0043995 | 0.006898 | 0.0064941 | 1.5185
1139 | - | - | 7 | 0.44163 | 38.02 | 45.6001 | 13.8982 | 13.1769 | 13.1769 | 7.0379 | 0.0043995 | 0.0043802 | 0.0064941 | 0.010496 | 1.9372
1144 | - | - | 7 | 0.44163 | 38.02 | 45.6345 | 13.9087 | 13.1874 | 13.1874 | 7.0423 | 0.0043802 | 0.0043611 | 0.010496 | 0.0134 | 2.7352
1149 | - | - | 7 | 0.44163 | 38.02 | 45.6785 | 13.9221 | 13.2008 | 13.2008 | 7.0466 | 0.0043611 | 0.0043422 | 0.0134 | 0.011506 | 2.8608
1154 | - | - | 7 | 0.44163 | 38.02 | 45.7162 | 13.9336 | 13.2123 | 13.2123 | 7.051 | 0.0043422 | 0.0043234 | 0.011506 | 0.0053882 | 1.9465
1159 | - | - | 7 | 0.44163 | 38.02 | 45.7339 | 13.939 | 13.2176 | 13.2176 | 7.0553 | 0.0043234 | 0.0043048 | 0.0053882 | -0.00030198 | 0.58665
1164 | - | - | 7 | 0.44163 | 38.02 | 45.7329 | 13.9387 | 13.2173 | 13.2173 | 7.0596 | 0.0043048 | 0.0042863 | -0.00030198 | 0.007196 | 0.80622
1169 | - | - | 7 | 0.44163 | 38.02 | 45.7565 | 13.9459 | 13.2245 | 13.2245 | 7.0639 | 0.0042863 | 0.004268 | 0.007196 | 0.0065119 | 1.6021 | 0.033645 | 0.03255 | 0.058234 | 0.033663 | 1.3768
1174 | - | - | 7 | 0.44163 | 38.02 | 45.7779 | 13.9524 | 13.2311 | 13.2311 | 7.0682 | 0.004268 | 0.0042499 | 0.0065119 | 0.017214 | 2.7908
1179 | - | - | 7 | 0.44163 | 38.02 | 45.8344 | 13.9696 | 13.2483 | 13.2483 | 7.0724 | 0.0042499 | 0.0042319 | 0.017214 | 0.0065901 | 2.8012
1184 | - | - | 7 | 0.44163 | 38.02 | 45.856 | 13.9762 | 13.2549 | 13.2549 | 7.0767 | 0.0042319 | 0.0042141 | 0.0065901 | -0.00060198 | 0.7054
1189 | - | - | 7 | 0.44163 | 38.02 | 45.854 | 13.9756 | 13.2543 | 13.2543 | 7.0809 | 0.0042141 | 0.0041964 | -0.00060198 | 0.007598 | 0.83593
1194 | - | - | 7 | 0.44163 | 38.02 | 45.879 | 13.9832 | 13.2619 | 13.2619 | 7.0851 | 0.0041964 | 0.0041789 | 0.007598 | 0.0076862 | 1.825
1199 | - | - | 7 | 0.44163 | 38.02 | 45.9042 | 13.9909 | 13.2695 | 13.2695 | 7.0892 | 0.0041789 | 0.0041615 | 0.0076862 | 0.011326 | 2.2813
1204 | - | - | 7 | 0.44163 | 38.02 | 45.9413 | 14.0022 | 13.2809 | 13.2809 | 7.0934 | 0.0041615 | 0.0041442 | 0.011326 | 0.0019099 | 1.5889
1209 | - | - | 7 | 0.44163 | 38.02 | 45.9476 | 14.0041 | 13.2828 | 13.2828 | 7.0975 | 0.0041442 | 0.0041271 | 0.0019099 | -0.009598 | -0.93525 | 0.03255 | 0.031523 | 0.033663 | 0.043802 | 1.2147
1214 | - | - | 7 | 0.44163 | 38.02 | 45.9161 | 13.9945 | 13.2732 | 13.2732 | 7.1017 | 0.0041271 | 0.0041102 | -0.009598 | 0.0078059 | -0.20886
1219 | - | - | 7 | 0.44163 | 38.02 | 45.9417 | 14.0024 | 13.281 | 13.281 | 7.1058 | 0.0041102 | 0.0040933 | 0.0078059 | 0.022418 | 3.6916
1224 | - | - | 7 | 0.44163 | 38.02 | 46.0153 | 14.0248 | 13.3034 | 13.3034 | 7.1099 | 0.0040933 | 0.0040766 | 0.022418 | 0.015706 | 4.663
1229 | - | - | 7 | 0.44163 | 38.02 | 46.0668 | 14.0405 | 13.3191 | 13.3191 | 7.114 | 0.0040766 | 0.0040601 | 0.015706 | -0.0051921 | 1.2817
1234 | - | - | 7 | 0.44163 | 38.02 | 46.0498 | 14.0353 | 13.3139 | 13.3139 | 7.118 | 0.0040601 | 0.0040437 | -0.0051921 | -0.0048921 | -1.2442
1239 | - | - | 7 | 0.44163 | 38.02 | 46.0337 | 14.0304 | 13.309 | 13.309 | 7.1221 | 0.0040437 | 0.0040274 | -0.0048921 | 0.0074039 | 0.31737
1244 | - | - | 7 | 0.44163 | 38.02 | 46.058 | 14.0378 | 13.3164 | 13.3164 | 7.1261 | 0.0040274 | 0.0040112 | 0.0074039 | 1.184e-05 | 0.91883
1249 | - | - | 7 | 0.44163 | 38.02 | 46.0581 | 14.0378 | 13.3164 | 13.3164 | 7.1301 | 0.0040112 | 0.0039952 | 1.184e-05 | 0.0017822 | 0.22497 | 0.031523 | 0.03056 | 0.043802 | 0.050288 | 1.5195
1254 | - | - | 7 | 0.44163 | 38.02 | 46.0639 | 14.0396 | 13.3182 | 13.3182 | 7.1341 | 0.0039952 | 0.0039793 | 0.0017822 | 0.003002 | 0.60055
1259 | - | - | 7 | 0.44163 | 38.02 | 46.0738 | 14.0426 | 13.3212 | 13.3212 | 7.1381 | 0.0039793 | 0.0039635 | 0.003002 | 0.0072138 | 1.2883
1264 | - | - | 7 | 0.44163 | 38.02 | 46.0974 | 14.0498 | 13.3284 | 13.3284 | 7.142 | 0.0039635 | 0.0039479 | 0.0072138 | 0.008002 | 1.9237
1269 | - | - | 7 | 0.44163 | 38.02 | 46.1237 | 14.0578 | 13.3364 | 13.3364 | 7.146 | 0.0039479 | 0.0039324 | 0.008002 | -0.00039605 | 0.96099
1274 | - | - | 7 | 0.44163 | 38.02 | 46.1224 | 14.0574 | 13.336 | 13.336 | 7.1499 | 0.0039324 | 0.003917 | -0.00039605 | 0.0051039 | 0.60254
1279 | - | - | 7 | 0.44163 | 38.02 | 46.1391 | 14.0625 | 13.3411 | 13.3411 | 7.1538 | 0.003917 | 0.0039017 | 0.0051039 | 0.0087941 | 1.7794
1284 | - | - | 7 | 0.44163 | 38.02 | 46.168 | 14.0713 | 13.3499 | 13.3499 | 7.1577 | 0.0039017 | 0.0038865 | 0.0087941 | 0.0103 | 2.4524
1289 | - | - | 7 | 0.44163 | 38.02 | 46.2018 | 14.0816 | 13.3602 | 13.3602 | 7.1616 | 0.0038865 | 0.0038715 | 0.0103 | 0.0045783 | 1.915 | 0.03056 | 0.029654 | 0.050288 | 0.063389 | 1.8953
1294 | - | - | 7 | 0.44163 | 38.02 | 46.2168 | 14.0862 | 13.3648 | 13.3648 | 7.1655 | 0.0038715 | 0.0038565 | 0.0045783 | 0.0049427 | 1.2322
1299 | - | - | 7 | 0.44163 | 38.02 | 46.233 | 14.0911 | 13.3698 | 13.3698 | 7.1694 | 0.0038565 | 0.0038417 | 0.0049427 | -0.01093 | -0.78563
1304 | - | - | 7 | 0.44163 | 38.02 | 46.1971 | 14.0802 | 13.3588 | 13.3588 | 7.1732 | 0.0038417 | 0.003827 | -0.01093 | 0.0018862 | -1.1729
1309 | - | - | 7 | 0.44163 | 38.02 | 46.2033 | 14.0821 | 13.3607 | 13.3607 | 7.177 | 0.003827 | 0.0038124 | 0.0018862 | 0.0048375 | 0.88161
1314 | - | - | 7 | 0.44163 | 38.02 | 46.2192 | 14.0869 | 13.3656 | 13.3656 | 7.1808 | 0.0038124 | 0.003798 | 0.0048375 | 0.0042316 | 1.1914
1319 | - | - | 7 | 0.44163 | 38.02 | 46.2331 | 14.0912 | 13.3698 | 13.3698 | 7.1846 | 0.003798 | 0.0037836 | 0.0042316 | 0.031926 | 4.783
1324 | - | - | 7 | 0.44163 | 38.02 | 46.3378 | 14.1231 | 13.4017 | 13.4017 | 7.1884 | 0.0037836 | 0.0037693 | 0.031926 | 0.0088158 | 5.3826
1329 | - | - | 7 | 0.44163 | 38.02 | 46.3668 | 14.1319 | 13.4105 | 13.4105 | 7.1922 | 0.0037693 | 0.0037552 | 0.0088158 | 0.0080197 | 2.237 | 0.029654 | 0.0288 | 0.063389 | 0.047298 | 1.8864
1334 | - | - | 7 | 0.44163 | 38.02 | 46.3931 | 14.1399 | 13.4185 | 13.4185 | 7.1959 | 0.0037552 | 0.0037411 | 0.0080197 | 0.011512 | 2.6073
1339 | - | - | 7 | 0.44163 | 38.02 | 46.4308 | 14.1514 | 13.4301 | 13.4301 | 7.1997 | 0.0037411 | 0.0037272 | 0.011512 | 0.0079217 | 2.6004
1344 | - | - | 7 | 0.44163 | 38.02 | 46.4568 | 14.1594 | 13.438 | 13.438 | 7.2034 | 0.0037272 | 0.0037133 | 0.0079217 | 0.012239 | 2.7118
1349 | - | - | 7 | 0.44163 | 38.02 | 46.497 | 14.1716 | 13.4502 | 13.4502 | 7.2071 | 0.0037133 | 0.0036996 | 0.012239 | 0.0069118 | 2.5809
1354 | - | - | 7 | 0.44163 | 38.02 | 46.5197 | 14.1785 | 13.4571 | 13.4571 | 7.2108 | 0.0036996 | 0.003686 | 0.0069118 | 0.0018487 | 1.1836
1359 | - | - | 7 | 0.44163 | 38.02 | 46.5257 | 14.1804 | 13.459 | 13.459 | 7.2145 | 0.003686 | 0.0036724 | 0.0018487 | 0.0082217 | 1.3718
1364 | - | - | 7 | 0.44163 | 38.02 | 46.5527 | 14.1886 | 13.4672 | 13.4672 | 7.2182 | 0.0036724 | 0.003659 | 0.0082217 | 0.0067138 | 2.0365
1369 | - | - | 7 | 0.44163 | 38.02 | 46.5747 | 14.1953 | 13.4739 | 13.4739 | 7.2218 | 0.003659 | 0.0036456 | 0.0067138 | 0.0049941 | 1.602 | 0.0288 | 0.027993 | 0.047298 | 0.033882 | 1.4233
1374 | - | - | 7 | 0.44163 | 38.02 | 46.5911 | 14.2003 | 13.4789 | 13.4789 | 7.2255 | 0.0036456 | 0.0036324 | 0.0049941 | 0.0081158 | 1.8029
1379 | - | - | 7 | 0.44163 | 38.02 | 46.6178 | 14.2084 | 13.487 | 13.487 | 7.2291 | 0.0036324 | 0.0036193 | 0.0081158 | 0.0015901 | 1.3352
1384 | - | - | 7 | 0.44163 | 38.02 | 46.623 | 14.21 | 13.4886 | 13.4886 | 7.2327 | 0.0036193 | 0.0036062 | 0.0015901 | 0.0064783 | 1.1191
1389 | - | - | 7 | 0.44163 | 38.02 | 46.6442 | 14.2165 | 13.4951 | 13.4951 | 7.2363 | 0.0036062 | 0.0035932 | 0.0064783 | -0.0016961 | 0.66017
1394 | - | - | 7 | 0.44163 | 38.02 | 46.6387 | 14.2148 | 13.4934 | 13.4934 | 7.2399 | 0.0035932 | 0.0035804 | -0.0016961 | 0.011412 | 1.3609
1399 | - | - | 7 | 0.44163 | 38.02 | 46.6761 | 14.2262 | 13.5048 | 13.5048 | 7.2435 | 0.0035804 | 0.0035676 | 0.011412 | 0.01209 | 3.2883
1404 | - | - | 7 | 0.44163 | 38.02 | 46.7158 | 14.2383 | 13.5169 | 13.5169 | 7.2471 | 0.0035676 | 0.0035549 | 0.01209 | 0.0043138 | 2.2992
1409 | - | - | 7 | 0.44163 | 38.02 | 46.7299 | 14.2426 | 13.5212 | 13.5212 | 7.2506 | 0.0035549 | 0.0035423 | 0.0043138 | 0.0071783 | 1.6207 | 0.027993 | 0.027231 | 0.033882 | -0.022266 | 0.18235
1414 | - | - | 7 | 0.44163 | 38.02 | 46.7535 | 14.2498 | 13.5284 | 13.5284 | 7.2542 | 0.0035423 | 0.0035298 | 0.0071783 | 0.00030198 | 1.0543
1419 | - | - | 7 | 0.44163 | 38.02 | 46.7545 | 14.2501 | 13.5287 | 13.5287 | 7.2577 | 0.0035298 | 0.0035174 | 0.00030198 | 0.0041881 | 0.63909
1424 | - | - | 7 | 0.44163 | 38.02 | 46.7682 | 14.2543 | 13.5329 | 13.5329 | 7.2612 | 0.0035174 | 0.0035051 | 0.0041881 | 0.002004 | 0.88066
1429 | - | - | 7 | 0.44163 | 38.02 | 46.7748 | 14.2563 | 13.5349 | 13.5349 | 7.2647 | 0.0035051 | 0.0034928 | 0.002004 | 0.0067099 | 1.2476
1434 | - | - | 7 | 0.44163 | 38.02 | 46.7968 | 14.263 | 13.5416 | 13.5416 | 7.2682 | 0.0034928 | 0.0034807 | 0.0067099 | 0.011708 | 2.6436
1439 | - | - | 7 | 0.44163 | 38.02 | 46.8352 | 14.2747 | 13.5533 | 13.5533 | 7.2717 | 0.0034807 | 0.0034686 | 0.011708 | 0.00091184 | 1.8106
1444 | - | - | 7 | 0.44163 | 38.02 | 46.8382 | 14.2756 | 13.5542 | 13.5542 | 7.2752 | 0.0034686 | 0.0034566 | 0.00091184 | 0.00088026 | 0.25876
1449 | - | - | 7 | 0.44163 | 38.02 | 46.8411 | 14.2765 | 13.5551 | 13.5551 | 7.2786 | 0.0034566 | 0.0034447 | 0.00088026 | 0.0091822 | 1.4622 | 0.027231 | 0.026509 | -0.022266 | 0.23702 | 4.1273
1454 | - | - | 7 | 0.44163 | 38.02 | 46.8712 | 14.2857 | 13.5643 | 13.5643 | 7.2821 | 0.0034447 | 0.0034329 | 0.0091822 | -0.004096 | 0.73289
1459 | - | - | 7 | 0.44163 | 38.02 | 46.8578 | 14.2816 | 13.5602 | 13.5602 | 7.2855 | 0.0034329 | 0.0034211 | -0.004096 | 0.014502 | 1.5275
1464 | - | - | 7 | 0.44163 | 38.02 | 46.9054 | 14.2961 | 13.5747 | 13.5747 | 7.2889 | 0.0034211 | 0.0034095 | 0.014502 | -0.045902 | -4.6272
1469 | - | - | 7 | 0.44163 | 38.02 | 46.7548 | 14.2502 | 13.5288 | 13.5288 | 7.2923 | 0.0034095 | 0.0033979 | -0.045902 | -0.016051 | -9.086
1474 | - | - | 7 | 0.44163 | 38.02 | 46.7021 | 14.2341 | 13.5127 | 13.5127 | 7.2957 | 0.0033979 | 0.0033864 | -0.016051 | 0.0013763 | -2.1544
1479 | - | - | 7 | 0.44163 | 38.02 | 46.7066 | 14.2355 | 13.5141 | 13.5141 | 7.2991 | 0.0033864 | 0.003375 | 0.0013763 | 0.0088566 | 1.5172
1484 | - | - | 7 | 0.44163 | 38.02 | 46.7357 | 14.2443 | 13.523 | 13.523 | 7.3025 | 0.003375 | 0.0033636 | 0.0088566 | 0.0098664 | 2.779
1489 | - | - | 7 | 0.44163 | 38.02 | 46.768 | 14.2542 | 13.5328 | 13.5328 | 7.3059 | 0.0033636 | 0.0033523 | 0.0098664 | 0.0090783 | 2.8205 | 0.026509 | 0.025825 | 0.23702 | 0.044075 | 5.2766
1494 | - | - | 7 | 0.44163 | 38.02 | 46.7978 | 14.2633 | 13.5419 | 13.5419 | 7.3092 | 0.0033523 | 0.0033411 | 0.0090783 | 0.011086 | 3.0136
1499 | - | - | 7 | 0.44163 | 38.02 | 46.8342 | 14.2744 | 13.553 | 13.553 | 7.3126 | 0.0033411 | 0.00333 | 0.011086 | 0.040786 | 7.7905
1504 | - | - | 7 | 0.44163 | 38.02 | 46.968 | 14.3152 | 13.5938 | 13.5938 | 7.3159 | 0.00333 | 0.003319 | 0.040786 | 0.0814 | 18.3971
1509 | - | - | 7 | 0.44163 | 38.02 | 47.2351 | 14.3966 | 13.6752 | 13.6752 | 7.3192 | 0.003319 | 0.003308 | 0.0814 | 0.038941 | 18.1383
1514 | - | - | 7 | 0.44163 | 38.02 | 47.3629 | 14.4355 | 13.7141 | 13.7141 | 7.3225 | 0.003308 | 0.0032971 | 0.038941 | 0.013378 | 7.9084
1519 | - | - | 7 | 0.44163 | 38.02 | 47.4068 | 14.4489 | 13.7275 | 13.7275 | 7.3258 | 0.0032971 | 0.0032862 | 0.013378 | 0.020457 | 5.1432
1524 | - | - | 7 | 0.44163 | 38.02 | 47.4739 | 14.4693 | 13.748 | 13.748 | 7.3291 | 0.0032862 | 0.0032755 | 0.020457 | 0.021894 | 6.4551
1529 | - | - | 7 | 0.44163 | 38.02 | 47.5457 | 14.4912 | 13.7699 | 13.7699 | 7.3324 | 0.0032755 | 0.0032648 | 0.021894 | 0.0092427 | 4.7545 | 0.025825 | 0.025174 | 0.044075 | 0.036425 | 1.5752
1534 | - | - | 7 | 0.44163 | 38.02 | 47.576 | 14.5005 | 13.7791 | 13.7791 | 7.3356 | 0.0032648 | 0.0032542 | 0.0092427 | 0.0069118 | 2.477
1539 | - | - | 7 | 0.44163 | 38.02 | 47.5987 | 14.5074 | 13.786 | 13.786 | 7.3389 | 0.0032542 | 0.0032436 | 0.0069118 | 0.0036842 | 1.6291
1544 | - | - | 7 | 0.44163 | 38.02 | 47.6108 | 14.5111 | 13.7897 | 13.7897 | 7.3421 | 0.0032436 | 0.0032331 | 0.0036842 | 0.0074467 | 1.7205
1549 | - | - | 7 | 0.44163 | 38.02 | 47.6352 | 14.5185 | 13.7971 | 13.7971 | 7.3454 | 0.0032331 | 0.0032227 | 0.0074467 | 0.00075854 | 1.2677
1554 | - | - | 7 | 0.44163 | 38.02 | 47.6377 | 14.5193 | 13.7979 | 13.7979 | 7.3486 | 0.0032227 | 0.0032123 | 0.00075854 | 0.0017743 | 0.39412
1559 | - | - | 7 | 0.44163 | 38.02 | 47.6435 | 14.521 | 13.7997 | 13.7997 | 7.3518 | 0.0032123 | 0.0032021 | 0.0017743 | 0.0060625 | 1.2239
1564 | - | - | 7 | 0.44163 | 38.02 | 47.6634 | 14.5271 | 13.8057 | 13.8057 | 7.355 | 0.0032021 | 0.0031918 | 0.0060625 | 0.0081941 | 2.2308
1569 | - | - | 7 | 0.44163 | 38.02 | 47.6903 | 14.5353 | 13.8139 | 13.8139 | 7.3582 | 0.0031918 | 0.0031817 | 0.0081941 | 0.0018822 | 1.5778 | 0.025174 | 0.024556 | 0.036425 | 0.039023 | 1.5189
1574 | - | - | 7 | 0.44163 | 38.02 | 47.6965 | 14.5372 | 13.8158 | 13.8158 | 7.3614 | 0.0031817 | 0.0031716 | 0.0018822 | 0.0050921 | 1.0994
1579 | - | - | 7 | 0.44163 | 38.02 | 47.7132 | 14.5423 | 13.8209 | 13.8209 | 7.3645 | 0.0031716 | 0.0031616 | 0.0050921 | 0.014418 | 3.0853
1584 | - | - | 7 | 0.44163 | 38.02 | 47.7605 | 14.5567 | 13.8353 | 13.8353 | 7.3677 | 0.0031616 | 0.0031516 | 0.014418 | 0.00097631 | 2.4317
1589 | - | - | 7 | 0.44163 | 38.02 | 47.7637 | 14.5577 | 13.8363 | 13.8363 | 7.3709 | 0.0031516 | 0.0031417 | 0.00097631 | 0.0045822 | 0.88506
1594 | - | - | 7 | 0.44163 | 38.02 | 47.7787 | 14.5623 | 13.8409 | 13.8409 | 7.374 | 0.0031417 | 0.0031319 | 0.0045822 | 0.0031941 | 1.2389
1599 | - | - | 7 | 0.44163 | 38.02 | 47.7892 | 14.5654 | 13.8441 | 13.8441 | 7.3771 | 0.0031319 | 0.0031221 | 0.0031941 | 0.011084 | 2.287
1604 | - | - | 7 | 0.44163 | 38.02 | 47.8256 | 14.5765 | 13.8552 | 13.8552 | 7.3803 | 0.0031221 | 0.0031124 | 0.011084 | -0.004804 | 0.99941
1609 | - | - | 7 | 0.44163 | 38.02 | 47.8098 | 14.5717 | 13.8504 | 13.8504 | 7.3834 | 0.0031124 | 0.0031027 | -0.004804 | 0.0081783 | 0.54942 | 0.024556 | 0.023968 | 0.039023 | 0.033041 | 1.4826
1614 | - | - | 7 | 0.44163 | 38.02 | 47.8367 | 14.5799 | 13.8585 | 13.8585 | 7.3865 | 0.0031027 | 0.0030931 | 0.0081783 | 0.01111 | 3.1146
1619 | - | - | 7 | 0.44163 | 38.02 | 47.8731 | 14.591 | 13.8696 | 13.8696 | 7.3896 | 0.0030931 | 0.0030836 | 0.01111 | -0.0048118 | 1.0117
1624 | - | - | 7 | 0.44163 | 38.02 | 47.8573 | 14.5862 | 13.8648 | 13.8648 | 7.3926 | 0.0030836 | 0.0030741 | -0.0048118 | 0.014792 | 1.6306
1629 | - | - | 7 | 0.44163 | 38.02 | 47.9059 | 14.601 | 13.8796 | 13.8796 | 7.3957 | 0.0030741 | 0.0030647 | 0.014792 | -0.0038158 | 1.7787
1634 | - | - | 7 | 0.44163 | 38.02 | 47.8933 | 14.5972 | 13.8758 | 13.8758 | 7.3988 | 0.0030647 | 0.0030553 | -0.0038158 | 0.001198 | -0.42524
1639 | - | - | 7 | 0.44163 | 38.02 | 47.8973 | 14.5984 | 13.877 | 13.877 | 7.4018 | 0.0030553 | 0.003046 | 0.001198 | 0.011 | 2.0042
1644 | - | - | 7 | 0.44163 | 38.02 | 47.9334 | 14.6094 | 13.888 | 13.888 | 7.4049 | 0.003046 | 0.0030367 | 0.011 | 0.0013724 | 2.0292
1649 | - | - | 7 | 0.44163 | 38.02 | 47.9379 | 14.6107 | 13.8894 | 13.8894 | 7.4079 | 0.0030367 | 0.0030276 | 0.0013724 | 0.0031862 | 0.75261 | 0.023968 | 0.023407 | 0.033041 | 0.088905 | 2.6028
1654 | - | - | 7 | 0.44163 | 38.02 | 47.9483 | 14.6139 | 13.8926 | 13.8926 | 7.411 | 0.0030276 | 0.0030184 | 0.0031862 | 0.0097961 | 2.1506
1659 | - | - | 7 | 0.44163 | 38.02 | 47.9805 | 14.6237 | 13.9024 | 13.9024 | 7.414 | 0.0030184 | 0.0030093 | 0.0097961 | 0.010814 | 3.4197
1664 | - | - | 7 | 0.44163 | 38.02 | 48.0159 | 14.6345 | 13.9132 | 13.9132 | 7.417 | 0.0030093 | 0.0030003 | 0.010814 | -0.0039138 | 1.1408
1669 | - | - | 7 | 0.44163 | 38.02 | 48.0031 | 14.6306 | 13.9093 | 13.9093 | 7.42 | 0.0030003 | 0.0029913 | -0.0039138 | 0.0065743 | 0.44929
1674 | - | - | 7 | 0.44163 | 38.02 | 48.0247 | 14.6372 | 13.9158 | 13.9158 | 7.423 | 0.0029913 | 0.0029824 | 0.0065743 | -0.0052079 | 0.22285
1679 | - | - | 7 | 0.44163 | 38.02 | 48.0076 | 14.632 | 13.9106 | 13.9106 | 7.426 | 0.0029824 | 0.0029735 | -0.0052079 | 0.0116 | 1.0816
1684 | - | - | 7 | 0.44163 | 38.02 | 48.0456 | 14.6436 | 13.9222 | 13.9222 | 7.4289 | 0.0029735 | 0.0029647 | 0.0116 | 0.0001921 | 1.9801
1689 | - | - | 7 | 0.44163 | 38.02 | 48.0463 | 14.6438 | 13.9224 | 13.9224 | 7.4319 | 0.0029647 | 0.002956 | 0.0001921 | 0.0024783 | 0.45217 | 0.023407 | 0.022871 | 0.088905 | 0.046251 | 2.9
1694 | - | - | 7 | 0.44163 | 38.02 | 48.0544 | 14.6463 | 13.9249 | 13.9249 | 7.4348 | 0.002956 | 0.0029472 | 0.0024783 | 0.008898 | 1.9304
1699 | - | - | 7 | 0.44163 | 38.02 | 48.0836 | 14.6552 | 13.9338 | 13.9338 | 7.4378 | 0.0029472 | 0.0029386 | 0.008898 | 0.041482 | 8.5759
1704 | - | - | 7 | 0.44163 | 38.02 | 48.2197 | 14.6966 | 13.9753 | 13.9753 | 7.4407 | 0.0029386 | 0.00293 | 0.041482 | 0.014092 | 9.4562
1709 | - | - | 7 | 0.44163 | 38.02 | 48.2659 | 14.7107 | 13.9894 | 13.9894 | 7.4437 | 0.00293 | 0.0029214 | 0.014092 | 0.0097961 | 4.0803
1714 | - | - | 7 | 0.44163 | 38.02 | 48.2981 | 14.7205 | 13.9992 | 13.9992 | 7.4466 | 0.0029214 | 0.0029129 | 0.0097961 | 0.00017828 | 1.7048
1719 | - | - | 7 | 0.44163 | 38.02 | 48.2987 | 14.7207 | 13.9993 | 13.9993 | 7.4495 | 0.0029129 | 0.0029044 | 0.00017828 | 0.010006 | 1.7556
1724 | - | - | 7 | 0.44163 | 38.02 | 48.3315 | 14.7307 | 14.0093 | 14.0093 | 7.4524 | 0.0029044 | 0.002896 | 0.010006 | 0.0019743 | 2.0614
1729 | - | - | 7 | 0.44163 | 38.02 | 48.338 | 14.7327 | 14.0113 | 14.0113 | 7.4553 | 0.002896 | 0.0028877 | 0.0019743 | 0.014492 | 2.8533 | 0.022871 | 0.02236 | 0.046251 | 0.031843 | 1.7198
1734 | - | - | 7 | 0.44163 | 38.02 | 48.3855 | 14.7472 | 14.0258 | 14.0258 | 7.4582 | 0.0028877 | 0.0028794 | 0.014492 | 0.012494 | 4.6784
1739 | - | - | 7 | 0.44163 | 38.02 | 48.4265 | 14.7597 | 14.0383 | 14.0383 | 7.4611 | 0.0028794 | 0.0028711 | 0.012494 | 0.00069803 | 2.2882
1744 | - | - | 7 | 0.44163 | 38.02 | 48.4288 | 14.7604 | 14.039 | 14.039 | 7.4639 | 0.0028711 | 0.0028629 | 0.00069803 | 0.0033921 | 0.71467
1749 | - | - | 7 | 0.44163 | 38.02 | 48.4399 | 14.7638 | 14.0424 | 14.0424 | 7.4668 | 0.0028629 | 0.0028547 | 0.0033921 | -0.0016079 | 0.30956
1754 | - | - | 7 | 0.44163 | 38.02 | 48.4347 | 14.7622 | 14.0408 | 14.0408 | 7.4697 | 0.0028547 | 0.0028466 | -0.0016079 | 0.0046099 | 0.52966
1759 | - | - | 7 | 0.44163 | 38.02 | 48.4498 | 14.7668 | 14.0454 | 14.0454 | 7.4725 | 0.0028466 | 0.0028385 | 0.0046099 | 0.0078842 | 2.1993
1764 | - | - | 7 | 0.44163 | 38.02 | 48.4756 | 14.7747 | 14.0533 | 14.0533 | 7.4753 | 0.0028385 | 0.0028305 | 0.0078842 | 0.0042881 | 2.1454
1769 | - | - | 7 | 0.44163 | 38.02 | 48.4897 | 14.7789 | 14.0576 | 14.0576 | 7.4782 | 0.0028305 | 0.0028225 | 0.0042881 | 0.0024941 | 1.1989 | 0.02236 | 0.021871 | 0.031843 | 0.038857 | 1.6023
1774 | - | - | 7 | 0.44163 | 38.02 | 48.4979 | 14.7814 | 14.0601 | 14.0601 | 7.481 | 0.0028225 | 0.0028145 | 0.0024941 | 0.0069 | 1.6687
1779 | - | - | 7 | 0.44163 | 38.02 | 48.5205 | 14.7883 | 14.067 | 14.067 | 7.4838 | 0.0028145 | 0.0028066 | 0.0069 | 0.0033842 | 1.8278
1784 | - | - | 7 | 0.44163 | 38.02 | 48.5316 | 14.7917 | 14.0704 | 14.0704 | 7.4866 | 0.0028066 | 0.0027988 | 0.0033842 | 0.0040941 | 1.3345
1789 | - | - | 7 | 0.44163 | 38.02 | 48.5451 | 14.7958 | 14.0744 | 14.0744 | 7.4894 | 0.0027988 | 0.002791 | 0.0040941 | 0.0026941 | 1.2137
1794 | - | - | 7 | 0.44163 | 38.02 | 48.5539 | 14.7985 | 14.0771 | 14.0771 | 7.4922 | 0.002791 | 0.0027832 | 0.0026941 | -0.00079802 | 0.33841
1799 | - | - | 7 | 0.44163 | 38.02 | 48.5513 | 14.7977 | 14.0763 | 14.0763 | 7.495 | 0.0027832 | 0.0027755 | -0.00079802 | 0.019686 | 3.4082
1804 | - | - | 7 | 0.44163 | 38.02 | 48.6159 | 14.8174 | 14.096 | 14.096 | 7.4978 | 0.0027755 | 0.0027678 | 0.019686 | -0.0066118 | 2.3455
1809 | - | - | 7 | 0.44163 | 38.02 | 48.5942 | 14.8108 | 14.0894 | 14.0894 | 7.5005 | 0.0027678 | 0.0027601 | -0.0066118 | 0.0092881 | 0.4921 | 0.021871 | 0.021403 | 0.038857 | 0.022664 | 1.4139
1814 | - | - | 7 | 0.44163 | 38.02 | 48.6247 | 14.8201 | 14.0987 | 14.0987 | 7.5033 | 0.0027601 | 0.0027525 | 0.0092881 | -0.008198 | 0.18901
1819 | - | - | 7 | 0.44163 | 38.02 | 48.5978 | 14.8119 | 14.0905 | 14.0905 | 7.506 | 0.0027525 | 0.002745 | -0.008198 | 0.01399 | 1.0647
1824 | - | - | 7 | 0.44163 | 38.02 | 48.6437 | 14.8259 | 14.1045 | 14.1045 | 7.5088 | 0.002745 | 0.0027375 | 0.01399 | 0.0052961 | 3.5135
1829 | - | - | 7 | 0.44163 | 38.02 | 48.661 | 14.8312 | 14.1098 | 14.1098 | 7.5115 | 0.0027375 | 0.00273 | 0.0052961 | -0.0027 | 0.47082
1834 | - | - | 7 | 0.44163 | 38.02 | 48.6522 | 14.8285 | 14.1071 | 14.1071 | 7.5143 | 0.00273 | 0.0027226 | -0.0027 | -0.0082138 | -2.0044
1839 | - | - | 7 | 0.44163 | 38.02 | 48.6252 | 14.8202 | 14.0989 | 14.0989 | 7.517 | 0.0027226 | 0.0027152 | -0.0082138 | 0.024596 | 3.0291
1844 | - | - | 7 | 0.44163 | 38.02 | 48.7059 | 14.8448 | 14.1235 | 14.1235 | 7.5197 | 0.0027152 | 0.0027078 | 0.024596 | 0.004798 | 5.4104
1849 | - | - | 7 | 0.44163 | 38.02 | 48.7217 | 14.8496 | 14.1283 | 14.1283 | 7.5224 | 0.0027078 | 0.0027005 | 0.004798 | 0.004596 | 1.7369 | 0.021403 | 0.020954 | 0.022664 | 0.045596 | 1.6234
1854 | - | - | 7 | 0.44163 | 38.02 | 48.7368 | 14.8542 | 14.1329 | 14.1329 | 7.5251 | 0.0027005 | 0.0026932 | 0.004596 | 0.004698 | 1.7232
1859 | - | - | 7 | 0.44163 | 38.02 | 48.7522 | 14.8589 | 14.1376 | 14.1376 | 7.5278 | 0.0026932 | 0.002686 | 0.004698 | -0.0045099 | 0.030375
1864 | - | - | 7 | 0.44163 | 38.02 | 48.7374 | 14.8544 | 14.1331 | 14.1331 | 7.5305 | 0.002686 | 0.0026788 | -0.0045099 | 0.0084 | 0.73158
1869 | - | - | 7 | 0.44163 | 38.02 | 48.7649 | 14.8628 | 14.1415 | 14.1415 | 7.5332 | 0.0026788 | 0.0026717 | 0.0084 | 0.00079407 | 1.7146
1874 | - | - | 7 | 0.44163 | 38.02 | 48.7675 | 14.8636 | 14.1423 | 14.1423 | 7.5358 | 0.0026717 | 0.0026645 | 0.00079407 | 0.0115 | 2.3093
1879 | - | - | 7 | 0.44163 | 38.02 | 48.8053 | 14.8751 | 14.1538 | 14.1538 | 7.5385 | 0.0026645 | 0.0026575 | 0.0115 | -0.012106 | -0.12566
1884 | - | - | 7 | 0.44163 | 38.02 | 48.7656 | 14.863 | 14.1416 | 14.1416 | 7.5412 | 0.0026575 | 0.0026504 | -0.012106 | 0.0092921 | -0.51942
1889 | - | - | 7 | 0.44163 | 38.02 | 48.796 | 14.8723 | 14.1509 | 14.1509 | 7.5438 | 0.0026504 | 0.0026434 | 0.0092921 | 0.0046941 | 2.6397 | 0.020954 | 0.020524 | 0.045596 | 0.037196 | 1.9923
1894 | - | - | 7 | 0.44163 | 38.02 | 48.8114 | 14.877 | 14.1556 | 14.1556 | 7.5464 | 0.0026434 | 0.0026364 | 0.0046941 | 0.010002 | 2.7861
1899 | - | - | 7 | 0.44163 | 38.02 | 48.8443 | 14.887 | 14.1656 | 14.1656 | 7.5491 | 0.0026364 | 0.0026295 | 0.010002 | -0.0010039 | 1.7032
1904 | - | - | 7 | 0.44163 | 38.02 | 48.841 | 14.886 | 14.1646 | 14.1646 | 7.5517 | 0.0026295 | 0.0026226 | -0.0010039 | 0.0036941 | 0.51455
1909 | - | - | 7 | 0.44163 | 38.02 | 48.8531 | 14.8897 | 14.1683 | 14.1683 | 7.5543 | 0.0026226 | 0.0026157 | 0.0036941 | 0.0054961 | 1.7553
1914 | - | - | 7 | 0.44163 | 38.02 | 48.8711 | 14.8952 | 14.1738 | 14.1738 | 7.557 | 0.0026157 | 0.0026089 | 0.0054961 | 0.017404 | 4.389
1919 | - | - | 7 | 0.44163 | 38.02 | 48.9282 | 14.9126 | 14.1912 | 14.1912 | 7.5596 | 0.0026089 | 0.0026021 | 0.017404 | 0.0021118 | 3.7374
1924 | - | - | 7 | 0.44163 | 38.02 | 48.9352 | 14.9147 | 14.1933 | 14.1933 | 7.5622 | 0.0026021 | 0.0025954 | 0.0021118 | 0.003198 | 1.0222
1929 | - | - | 7 | 0.44163 | 38.02 | 48.9456 | 14.9179 | 14.1965 | 14.1965 | 7.5648 | 0.0025954 | 0.0025887 | 0.003198 | -0.005704 | -0.48784 | 0.020524 | 0.020111 | 0.037196 | 0.019541 | 1.3877
1934 | - | - | 7 | 0.44163 | 38.02 | 48.9269 | 14.9122 | 14.1908 | 14.1908 | 7.5673 | 0.0025887 | 0.002582 | -0.005704 | 0.003 | -0.51859
1939 | - | - | 7 | 0.44163 | 38.02 | 48.9368 | 14.9152 | 14.1938 | 14.1938 | 7.5699 | 0.002582 | 0.0025753 | 0.003 | 0.009996 | 2.5234
1944 | - | - | 7 | 0.44163 | 38.02 | 48.9696 | 14.9252 | 14.2038 | 14.2038 | 7.5725 | 0.0025753 | 0.0025687 | 0.009996 | -0.013796 | -0.75062
1949 | - | - | 7 | 0.44163 | 38.02 | 48.9243 | 14.9114 | 14.19 | 14.19 | 7.5751 | 0.0025687 | 0.0025621 | -0.013796 | 0.021398 | 1.4992
1954 | - | - | 7 | 0.44163 | 38.02 | 48.9945 | 14.9328 | 14.2114 | 14.2114 | 7.5776 | 0.0025621 | 0.0025556 | 0.021398 | 0.013198 | 6.756
1959 | - | - | 7 | 0.44163 | 38.02 | 49.0378 | 14.946 | 14.2246 | 14.2246 | 7.5802 | 0.0025556 | 0.0025491 | 0.013198 | 0.0108 | 4.7
1964 | - | - | 7 | 0.44163 | 38.02 | 49.0732 | 14.9568 | 14.2354 | 14.2354 | 7.5827 | 0.0025491 | 0.0025426 | 0.0108 | -0.0016961 | 1.7818
1969 | - | - | 7 | 0.44163 | 38.02 | 49.0677 | 14.9551 | 14.2337 | 14.2337 | 7.5853 | 0.0025426 | 0.0025361 | -0.0016961 | 0.0077138 | 1.1896 | 0.020111 | 0.019715 | 0.019541 | 0.036679 | 1.4205
1974 | - | - | 7 | 0.44163 | 38.02 | 49.093 | 14.9628 | 14.2414 | 14.2414 | 7.5878 | 0.0025361 | 0.0025297 | 0.0077138 | 0.002998 | 2.1122
1979 | - | - | 7 | 0.44163 | 38.02 | 49.1028 | 14.9658 | 14.2444 | 14.2444 | 7.5903 | 0.0025297 | 0.0025233 | 0.002998 | -0.0096059 | -1.314
1984 | - | - | 7 | 0.44163 | 38.02 | 49.0713 | 14.9562 | 14.2348 | 14.2348 | 7.5929 | 0.0025233 | 0.002517 | -0.0096059 | 0.0023039 | -1.4428
1989 | - | - | 7 | 0.44163 | 38.02 | 49.0789 | 14.9585 | 14.2371 | 14.2371 | 7.5954 | 0.002517 | 0.0025107 | 0.0023039 | 0.018818 | 4.2094
1994 | - | - | 7 | 0.44163 | 38.02 | 49.1406 | 14.9773 | 14.256 | 14.256 | 7.5979 | 0.0025107 | 0.0025044 | 0.018818 | 0.0078079 | 5.3037
1999 | - | - | 7 | 0.44163 | 38.02 | 49.1662 | 14.9851 | 14.2638 | 14.2638 | 7.6004 | 0.0025044 | 0.0024981 | 0.0078079 | -0.0039059 | 0.77415
2004 | - | - | 7 | 0.44163 | 38.02 | 49.1534 | 14.9812 | 14.2599 | 14.2599 | 7.6029 | 0.0024981 | 0.0024919 | -0.0039059 | -0.0065882 | -2.1044
2009 | - | - | 7 | 0.44163 | 38.02 | 49.1318 | 14.9746 | 14.2533 | 14.2533 | 7.6054 | 0.0024919 | 0.0024857 | -0.0065882 | 0.008402 | 0.37189 | 0.019715 | 0.019334 | 0.036679 | 0.033645 | 1.7998
2014 | - | - | 7 | 0.44163 | 38.02 | 49.1594 | 14.983 | 14.2617 | 14.2617 | 7.6079 | 0.0024857 | 0.0024795 | 0.008402 | -0.0013901 | 1.4073
2019 | - | - | 7 | 0.44163 | 38.02 | 49.1548 | 14.9817 | 14.2603 | 14.2603 | 7.6104 | 0.0024795 | 0.0024734 | -0.0013901 | 0.0019138 | 0.10739
2024 | - | - | 7 | 0.44163 | 38.02 | 49.1611 | 14.9836 | 14.2622 | 14.2622 | 7.6128 | 0.0024734 | 0.0024673 | 0.0019138 | 0.017304 | 3.8974
2029 | - | - | 7 | 0.44163 | 38.02 | 49.2179 | 15.0009 | 14.2795 | 14.2795 | 7.6153 | 0.0024673 | 0.0024612 | 0.017304 | -0.0025822 | 2.9771
2034 | - | - | 7 | 0.44163 | 38.02 | 49.2094 | 14.9983 | 14.2769 | 14.2769 | 7.6178 | 0.0024612 | 0.0024552 | -0.0025822 | 0.0085197 | 1.2132
2039 | - | - | 7 | 0.44163 | 38.02 | 49.2373 | 15.0068 | 14.2854 | 14.2854 | 7.6202 | 0.0024552 | 0.0024492 | 0.0085197 | 0.0028 | 2.3052
2044 | - | - | 7 | 0.44163 | 38.02 | 49.2465 | 15.0096 | 14.2882 | 14.2882 | 7.6227 | 0.0024492 | 0.0024432 | 0.0028 | 0.0017118 | 0.92168
2049 | - | - | 7 | 0.44163 | 38.02 | 49.2521 | 15.0113 | 14.29 | 14.29 | 7.6251 | 0.0024432 | 0.0024372 | 0.0017118 | 0.0089217 | 2.1824 | 0.019334 | 0.018967 | 0.033645 | 0.051241 | 2.2255
2054 | - | - | 7 | 0.44163 | 38.02 | 49.2814 | 15.0202 | 14.2989 | 14.2989 | 7.6275 | 0.0024372 | 0.0024313 | 0.0089217 | -0.0097079 | -0.1708
2059 | - | - | 7 | 0.44163 | 38.02 | 49.2496 | 15.0105 | 14.2892 | 14.2892 | 7.63 | 0.0024313 | 0.0024254 | -0.0097079 | 0.012808 | 0.64955
2064 | - | - | 7 | 0.44163 | 38.02 | 49.2916 | 15.0233 | 14.302 | 14.302 | 7.6324 | 0.0024254 | 0.0024196 | 0.012808 | 0.0042099 | 3.5082
2069 | - | - | 7 | 0.44163 | 38.02 | 49.3054 | 15.0276 | 14.3062 | 14.3062 | 7.6348 | 0.0024196 | 0.0024137 | 0.0042099 | -0.003698 | 0.10195
2074 | - | - | 7 | 0.44163 | 38.02 | 49.2933 | 15.0239 | 14.3025 | 14.3025 | 7.6372 | 0.0024137 | 0.0024079 | -0.003698 | 0.0062059 | 0.52509
2079 | - | - | 7 | 0.44163 | 38.02 | 49.3136 | 15.0301 | 14.3087 | 14.3087 | 7.6396 | 0.0024079 | 0.0024021 | 0.0062059 | 0.0172 | 4.8716
2084 | - | - | 7 | 0.44163 | 38.02 | 49.3701 | 15.0473 | 14.3259 | 14.3259 | 7.642 | 0.0024021 | 0.0023964 | 0.0172 | -0.0022941 | 3.0967
2089 | - | - | 7 | 0.44163 | 38.02 | 49.3625 | 15.045 | 14.3236 | 14.3236 | 7.6444 | 0.0023964 | 0.0023906 | -0.0022941 | 0.013906 | 2.4338 | 0.018967 | 0.018614 | 0.051241 | 0.10844 | 4.2785
2094 | - | - | 7 | 0.44163 | 38.02 | 49.4082 | 15.0589 | 14.3375 | 14.3375 | 7.6468 | 0.0023906 | 0.0023849 | 0.013906 | 0.0091783 | 4.8315
2099 | - | - | 7 | 0.44163 | 38.02 | 49.4383 | 15.0681 | 14.3467 | 14.3467 | 7.6492 | 0.0023849 | 0.0023793 | 0.0091783 | 0.010828 | 4.2001
2104 | - | - | 7 | 0.44163 | 38.02 | 49.4738 | 15.0789 | 14.3575 | 14.3575 | 7.6516 | 0.0023793 | 0.0023736 | 0.010828 | -0.001998 | 1.8513
2109 | - | - | 7 | 0.44163 | 38.02 | 49.4672 | 15.0769 | 14.3555 | 14.3555 | 7.654 | 0.0023736 | 0.002368 | -0.001998 | -0.0042921 | -1.3277
2114 | - | - | 7 | 0.44163 | 38.02 | 49.4532 | 15.0726 | 14.3512 | 14.3512 | 7.6563 | 0.002368 | 0.0023624 | -0.0042921 | 0.0083099 | 0.85566
2119 | - | - | 7 | 0.44163 | 38.02 | 49.4804 | 15.0809 | 14.3595 | 14.3595 | 7.6587 | 0.0023624 | 0.0023568 | 0.0083099 | 0.0039059 | 2.5863
2124 | - | - | 7 | 0.44163 | 38.02 | 49.4932 | 15.0848 | 14.3634 | 14.3634 | 7.6611 | 0.0023568 | 0.0023513 | 0.0039059 | 0.011404 | 3.2556
2129 | - | - | 7 | 0.44163 | 38.02 | 49.5307 | 15.0962 | 14.3748 | 14.3748 | 7.6634 | 0.0023513 | 0.0023458 | 0.011404 | 0.0034 | 3.1478 | 0.018614 | 0.018274 | 0.10844 | 0.058302 | 4.4961
2134 | - | - | 7 | 0.44163 | 38.02 | 49.5418 | 15.0996 | 14.3782 | 14.3782 | 7.6658 | 0.0023458 | 0.0023403 | 0.0034 | -0.0053862 | -0.42824
2139 | - | - | 7 | 0.44163 | 38.02 | 49.5241 | 15.0942 | 14.3729 | 14.3729 | 7.6681 | 0.0023403 | 0.0023348 | -0.0053862 | 0.01021 | 1.0396
2144 | - | - | 7 | 0.44163 | 38.02 | 49.5576 | 15.1044 | 14.3831 | 14.3831 | 7.6704 | 0.0023348 | 0.0023294 | 0.01021 | 0.030902 | 8.8247
2149 | - | - | 7 | 0.44163 | 38.02 | 49.659 | 15.1353 | 14.414 | 14.414 | 7.6728 | 0.0023294 | 0.002324 | 0.030902 | 0.0069 | 8.1117
2154 | - | - | 7 | 0.44163 | 38.02 | 49.6817 | 15.1422 | 14.4209 | 14.4209 | 7.6751 | 0.002324 | 0.0023186 | 0.0069 | 0.011814 | 4.0334
2159 | - | - | 7 | 0.44163 | 38.02 | 49.7204 | 15.154 | 14.4327 | 14.4327 | 7.6774 | 0.0023186 | 0.0023132 | 0.011814 | 0.026502 | 8.2797
2164 | - | - | 7 | 0.44163 | 38.02 | 49.8074 | 15.1805 | 14.4592 | 14.4592 | 7.6797 | 0.0023132 | 0.0023079 | 0.026502 | 0.024102 | 10.9495
2169 | - | - | 7 | 0.44163 | 38.02 | 49.8865 | 15.2047 | 14.4833 | 14.4833 | 7.682 | 0.0023079 | 0.0023026 | 0.024102 | 0.0094941 | 7.2797 | 0.018274 | 0.017946 | 0.058302 | -0.026524 | 0.83511
2174 | - | - | 7 | 0.44163 | 38.02 | 49.9176 | 15.2141 | 14.4928 | 14.4928 | 7.6843 | 0.0023026 | 0.0022973 | 0.0094941 | 0.010902 | 4.4348
2179 | - | - | 7 | 0.44163 | 38.02 | 49.9534 | 15.225 | 14.5037 | 14.5037 | 7.6866 | 0.0022973 | 0.002292 | 0.010902 | 0.007098 | 3.9203
2184 | - | - | 7 | 0.44163 | 38.02 | 49.9767 | 15.2321 | 14.5108 | 14.5108 | 7.6889 | 0.002292 | 0.0022868 | 0.007098 | 0.0142 | 4.655
2189 | - | - | 7 | 0.44163 | 38.02 | 50.0233 | 15.2463 | 14.525 | 14.525 | 7.6912 | 0.0022868 | 0.0022815 | 0.0142 | 0.002498 | 3.6494
2194 | - | - | 7 | 0.44163 | 38.02 | 50.0315 | 15.2488 | 14.5275 | 14.5275 | 7.6935 | 0.0022815 | 0.0022763 | 0.002498 | 0.010206 | 2.7911
2199 | - | - | 7 | 0.44163 | 38.02 | 50.0649 | 15.259 | 14.5377 | 14.5377 | 7.6958 | 0.0022763 | 0.0022712 | 0.010206 | -0.0047882 | 1.1839
2204 | - | - | 7 | 0.44163 | 38.02 | 50.0492 | 15.2543 | 14.5329 | 14.5329 | 7.698 | 0.0022712 | 0.002266 | -0.0047882 | 0.0086921 | 0.86717
2209 | - | - | 7 | 0.44163 | 38.02 | 50.0777 | 15.263 | 14.5416 | 14.5416 | 7.7003 | 0.002266 | 0.0022609 | 0.0086921 | 0.0066941 | 3.3978 | 0.017946 | 0.017629 | -0.026524 | -0.013566 | -1.1206
2214 | - | - | 7 | 0.44163 | 38.02 | 50.0997 | 15.2696 | 14.5483 | 14.5483 | 7.7026 | 0.0022609 | 0.0022558 | 0.0066941 | 0.010196 | 3.7412
2219 | - | - | 7 | 0.44163 | 38.02 | 50.1332 | 15.2798 | 14.5585 | 14.5585 | 7.7048 | 0.0022558 | 0.0022507 | 0.010196 | 0.012992 | 5.1469
2224 | - | - | 7 | 0.44163 | 38.02 | 50.1758 | 15.2928 | 14.5715 | 14.5715 | 7.7071 | 0.0022507 | 0.0022457 | 0.012992 | -0.0052 | 1.7239
2229 | - | - | 7 | 0.44163 | 38.02 | 50.1587 | 15.2876 | 14.5663 | 14.5663 | 7.7093 | 0.0022457 | 0.0022406 | -0.0052 | -0.0015 | -1.4916
2234 | - | - | 7 | 0.44163 | 38.02 | 50.1538 | 15.2861 | 14.5648 | 14.5648 | 7.7115 | 0.0022406 | 0.0022356 | -0.0015 | -0.0022099 | -0.82914
2239 | - | - | 7 | 0.44163 | 38.02 | 50.1466 | 15.2839 | 14.5626 | 14.5626 | 7.7138 | 0.0022356 | 0.0022307 | -0.0022099 | -0.010894 | -2.9383
2244 | - | - | 7 | 0.44163 | 38.02 | 50.1108 | 15.273 | 14.5517 | 14.5517 | 7.716 | 0.0022307 | 0.0022257 | -0.010894 | -0.036602 | -10.671
2249 | - | - | 7 | 0.44163 | 38.02 | 49.9907 | 15.2364 | 14.5151 | 14.5151 | 7.7182 | 0.0022257 | 0.0022207 | -0.036602 | -0.0086 | -10.1519 | 0.017629 | 0.017324 | -0.013566 | 0.028553 | 0.44989
2254 | - | - | 7 | 0.44163 | 38.02 | 49.9625 | 15.2278 | 14.5065 | 14.5065 | 7.7205 | 0.0022207 | 0.0022158 | -0.0086 | 0.002198 | -1.4376
2259 | - | - | 7 | 0.44163 | 38.02 | 49.9697 | 15.23 | 14.5087 | 14.5087 | 7.7227 | 0.0022158 | 0.0022109 | 0.002198 | -0.015194 | -2.9445
2264 | - | - | 7 | 0.44163 | 38.02 | 49.9199 | 15.2148 | 14.4935 | 14.4935 | 7.7249 | 0.0022109 | 0.002206 | -0.015194 | 0.0042059 | -2.478
2269 | - | - | 7 | 0.44163 | 38.02 | 49.9337 | 15.219 | 14.4977 | 14.4977 | 7.7271 | 0.002206 | 0.0022012 | 0.0042059 | 0.0046158 | 2.0019
2274 | - | - | 7 | 0.44163 | 38.02 | 49.9488 | 15.2237 | 14.5023 | 14.5023 | 7.7293 | 0.0022012 | 0.0021964 | 0.0046158 | 0.001898 | 1.4799
2279 | - | - | 7 | 0.44163 | 38.02 | 49.955 | 15.2256 | 14.5042 | 14.5042 | 7.7315 | 0.0021964 | 0.0021915 | 0.001898 | 0.011006 | 2.9454
2284 | - | - | 7 | 0.44163 | 38.02 | 49.9911 | 15.2366 | 14.5152 | 14.5152 | 7.7337 | 0.0021915 | 0.0021867 | 0.011006 | -0.013696 | -0.62678
2289 | - | - | 7 | 0.44163 | 38.02 | 49.9462 | 15.2229 | 14.5015 | 14.5015 | 7.7359 | 0.0021867 | 0.002182 | -0.013696 | 0.0040138 | -2.2074 | 0.017324 | 0.017029 | 0.028553 | 0.030255 | 1.713
2294 | - | - | 7 | 0.44163 | 38.02 | 49.9594 | 15.2269 | 14.5055 | 14.5055 | 7.7381 | 0.002182 | 0.0021772 | 0.0040138 | -0.00069013 | 0.7601
2299 | - | - | 7 | 0.44163 | 38.02 | 49.9571 | 15.2262 | 14.5048 | 14.5048 | 7.7402 | 0.0021772 | 0.0021725 | -0.00069013 | 0.010108 | 2.1705
2304 | - | - | 7 | 0.44163 | 38.02 | 49.9903 | 15.2363 | 14.5149 | 14.5149 | 7.7424 | 0.0021725 | 0.0021678 | 0.010108 | 0.00029408 | 2.3917
2309 | - | - | 7 | 0.44163 | 38.02 | 49.9912 | 15.2366 | 14.5152 | 14.5152 | 7.7446 | 0.0021678 | 0.0021631 | 0.00029408 | 0.0053039 | 1.2951
2314 | - | - | 7 | 0.44163 | 38.02 | 50.0086 | 15.2419 | 14.5205 | 14.5205 | 7.7467 | 0.0021631 | 0.0021584 | 0.0053039 | 0.0096099 | 3.4532
2319 | - | - | 7 | 0.44163 | 38.02 | 50.0402 | 15.2515 | 14.5301 | 14.5301 | 7.7489 | 0.0021584 | 0.0021538 | 0.0096099 | -0.012188 | -0.6088
2324 | - | - | 7 | 0.44163 | 38.02 | 50.0002 | 15.2393 | 14.5179 | 14.5179 | 7.751 | 0.0021538 | 0.0021492 | -0.012188 | 0.012102 | -0.0078836
2329 | - | - | 7 | 0.44163 | 38.02 | 50.0399 | 15.2514 | 14.53 | 14.53 | 7.7532 | 0.0021492 | 0.0021445 | 0.012102 | -0.0051941 | 1.6002 | 0.017029 | 0.016744 | 0.030255 | 0.031736 | 1.8365
2334 | - | - | 7 | 0.44163 | 38.02 | 50.0229 | 15.2462 | 14.5249 | 14.5249 | 7.7553 | 0.0021445 | 0.00214 | -0.0051941 | 0.010722 | 1.2981
2339 | - | - | 7 | 0.44163 | 38.02 | 50.058 | 15.2569 | 14.5356 | 14.5356 | 7.7575 | 0.00214 | 0.0021354 | 0.010722 | 0.013308 | 5.6218
2344 | - | - | 7 | 0.44163 | 38.02 | 50.1017 | 15.2703 | 14.5489 | 14.5489 | 7.7596 | 0.0021354 | 0.0021308 | 0.013308 | -0.0027921 | 2.4569
2349 | - | - | 7 | 0.44163 | 38.02 | 50.0925 | 15.2675 | 14.5461 | 14.5461 | 7.7617 | 0.0021308 | 0.0021263 | -0.0027921 | 0.011188 | 1.9792
2354 | - | - | 7 | 0.44163 | 38.02 | 50.1292 | 15.2786 | 14.5573 | 14.5573 | 7.7639 | 0.0021263 | 0.0021218 | 0.011188 | 0.0070039 | 4.2803
2359 | - | - | 7 | 0.44163 | 38.02 | 50.1522 | 15.2857 | 14.5643 | 14.5643 | 7.766 | 0.0021218 | 0.0021173 | 0.0070039 | -0.0073901 | -0.098297
2364 | - | - | 7 | 0.44163 | 38.02 | 50.128 | 15.2783 | 14.5569 | 14.5569 | 7.7681 | 0.0021173 | 0.0021128 | -0.0073901 | 0.0034099 | -0.93553
2369 | - | - | 7 | 0.44163 | 38.02 | 50.1392 | 15.2817 | 14.5603 | 14.5603 | 7.7702 | 0.0021128 | 0.0021084 | 0.0034099 | -0.0004 | 0.71113 | 0.016744 | 0.016468 | 0.031736 | 0.025234 | 1.7123
2374 | - | - | 7 | 0.44163 | 38.02 | 50.1379 | 15.2813 | 14.5599 | 14.5599 | 7.7723 | 0.0021084 | 0.0021039 | -0.0004 | 0.0071 | 1.5943
2379 | - | - | 7 | 0.44163 | 38.02 | 50.1611 | 15.2884 | 14.567 | 14.567 | 7.7744 | 0.0021039 | 0.0020995 | 0.0071 | 0.0044118 | 2.7373
2384 | - | - | 7 | 0.44163 | 38.02 | 50.1756 | 15.2928 | 14.5714 | 14.5714 | 7.7765 | 0.0020995 | 0.0020951 | 0.0044118 | 0.001198 | 1.3358
2389 | - | - | 7 | 0.44163 | 38.02 | 50.1796 | 15.294 | 14.5726 | 14.5726 | 7.7786 | 0.0020951 | 0.0020907 | 0.001198 | 0.0090138 | 2.4435
2394 | - | - | 7 | 0.44163 | 38.02 | 50.2091 | 15.303 | 14.5816 | 14.5816 | 7.7807 | 0.0020907 | 0.0020864 | 0.0090138 | 0.00050197 | 2.2738
2399 | - | - | 7 | 0.44163 | 38.02 | 50.2108 | 15.3035 | 14.5821 | 14.5821 | 7.7828 | 0.0020864 | 0.002082 | 0.00050197 | 0.012796 | 3.1963
2404 | - | - | 7 | 0.44163 | 38.02 | 50.2528 | 15.3163 | 14.5949 | 14.5949 | 7.7849 | 0.002082 | 0.0020777 | 0.012796 | -0.0028862 | 2.3745
2409 | - | - | 7 | 0.44163 | 38.02 | 50.2433 | 15.3134 | 14.592 | 14.592 | 7.787 | 0.0020777 | 0.0020734 | -0.0028862 | 0.0064079 | 0.85303 | 0.016468 | 0.016201 | 0.025234 | 0.0079079 | 1.0059
2414 | - | - | 7 | 0.44163 | 38.02 | 50.2643 | 15.3198 | 14.5984 | 14.5984 | 7.789 | 0.0020734 | 0.0020691 | 0.0064079 | 0.004502 | 2.6327
2419 | - | - | 7 | 0.44163 | 38.02 | 50.2791 | 15.3243 | 14.6029 | 14.6029 | 7.7911 | 0.0020691 | 0.0020648 | 0.004502 | -0.011106 | -1.6053
2424 | - | - | 7 | 0.44163 | 38.02 | 50.2426 | 15.3132 | 14.5918 | 14.5918 | 7.7932 | 0.0020648 | 0.0020606 | -0.011106 | 0.0077 | -0.81619
2429 | - | - | 7 | 0.44163 | 38.02 | 50.2679 | 15.3209 | 14.5995 | 14.5995 | 7.7952 | 0.0020606 | 0.0020563 | 0.0077 | 0.0085 | 3.9354
2434 | - | - | 7 | 0.44163 | 38.02 | 50.2958 | 15.3294 | 14.608 | 14.608 | 7.7973 | 0.0020563 | 0.0020521 | 0.0085 | -0.0086961 | -0.056317
2439 | - | - | 7 | 0.44163 | 38.02 | 50.2673 | 15.3207 | 14.5993 | 14.5993 | 7.7993 | 0.0020521 | 0.0020479 | -0.0086961 | 0.01892 | 2.5074
2444 | - | - | 7 | 0.44163 | 38.02 | 50.3293 | 15.3396 | 14.6183 | 14.6183 | 7.8014 | 0.0020479 | 0.0020437 | 0.01892 | -0.00099408 | 4.3711
2449 | - | - | 7 | 0.44163 | 38.02 | 50.3261 | 15.3386 | 14.6173 | 14.6173 | 7.8034 | 0.0020437 | 0.0020396 | -0.00099408 | -0.0031039 | -1.0047 | 0.016201 | 0.015943 | 0.0079079 | 0.023439 | 0.9831
2454 | - | - | 7 | 0.44163 | 38.02 | 50.3159 | 15.3355 | 14.6142 | 14.6142 | 7.8055 | 0.0020396 | 0.0020354 | -0.0031039 | 0.0053 | 0.54311
2459 | - | - | 7 | 0.44163 | 38.02 | 50.3333 | 15.3408 | 14.6195 | 14.6195 | 7.8075 | 0.0020354 | 0.0020313 | 0.0053 | 0.00060395 | 1.4494
2464 | - | - | 7 | 0.44163 | 38.02 | 50.3353 | 15.3414 | 14.6201 | 14.6201 | 7.8095 | 0.0020313 | 0.0020272 | 0.00060395 | -0.0027079 | -0.52007
2469 | - | - | 7 | 0.44163 | 38.02 | 50.3264 | 15.3387 | 14.6174 | 14.6174 | 7.8116 | 0.0020272 | 0.0020231 | -0.0027079 | 0.013104 | 2.5747
2474 | - | - | 7 | 0.44163 | 38.02 | 50.3694 | 15.3518 | 14.6305 | 14.6305 | 7.8136 | 0.0020231 | 0.002019 | 0.013104 | 0.0006 | 3.3841
2479 | - | - | 7 | 0.44163 | 38.02 | 50.3713 | 15.3524 | 14.6311 | 14.6311 | 7.8156 | 0.002019 | 0.0020149 | 0.0006 | -0.0013961 | -0.19834
2484 | - | - | 7 | 0.44163 | 38.02 | 50.3668 | 15.351 | 14.6297 | 14.6297 | 7.8176 | 0.0020149 | 0.0020109 | -0.0013961 | -0.0044921 | -1.4642
2489 | - | - | 7 | 0.44163 | 38.02 | 50.352 | 15.3465 | 14.6252 | 14.6252 | 7.8196 | 0.0020109 | 0.0020068 | -0.0044921 | 0.0066079 | 0.53217 | 0.015943 | 0.015693 | 0.023439 | 0.013136 | 1.1511
2494 | - | - | 7 | 0.44163 | 38.02 | 50.3737 | 15.3532 | 14.6318 | 14.6318 | 7.8216 | 0.0020068 | 0.0020028 | 0.0066079 | 0.0039039 | 2.6203
2499 | - | - | 7 | 0.44163 | 38.02 | 50.3865 | 15.3571 | 14.6357 | 14.6357 | 7.8236 | 0.0020028 | 0.0019988 | 0.0039039 | -0.0095961 | -1.4292
2504 | - | - | 7 | 0.44163 | 38.02 | 50.355 | 15.3475 | 14.6261 | 14.6261 | 7.8256 | 0.0019988 | 0.0019948 | -0.0095961 | 0.0222 | 3.1719
2509 | - | - | 7 | 0.44163 | 38.02 | 50.4279 | 15.3697 | 14.6483 | 14.6483 | 7.8276 | 0.0019948 | 0.0019908 | 0.0222 | -0.011904 | 2.5662
2514 | - | - | 7 | 0.44163 | 38.02 | 50.3888 | 15.3578 | 14.6364 | 14.6364 | 7.8296 | 0.0019908 | 0.0019869 | -0.011904 | -0.00099408 | -3.2371
2519 | - | - | 7 | 0.44163 | 38.02 | 50.3855 | 15.3568 | 14.6354 | 14.6354 | 7.8316 | 0.0019869 | 0.0019829 | -0.00099408 | 0.0083138 | 1.8485
2524 | - | - | 7 | 0.44163 | 38.02 | 50.4128 | 15.3651 | 14.6437 | 14.6437 | 7.8336 | 0.0019829 | 0.001979 | 0.0083138 | 0.0049079 | 3.3355
2529 | - | - | 7 | 0.44163 | 38.02 | 50.4289 | 15.37 | 14.6486 | 14.6486 | 7.8356 | 0.001979 | 0.0019751 | 0.0049079 | 0.0046079 | 2.4064 | 0.015693 | 0.01545 | 0.013136 | 0.022953 | 1.1639
2534 | - | - | 7 | 0.44163 | 38.02 | 50.444 | 15.3746 | 14.6532 | 14.6532 | 7.8376 | 0.0019751 | 0.0019712 | 0.0046079 | 0.0056941 | 2.6111
2539 | - | - | 7 | 0.44163 | 38.02 | 50.4627 | 15.3803 | 14.6589 | 14.6589 | 7.8395 | 0.0019712 | 0.0019673 | 0.0056941 | -0.0090842 | -0.86814
2544 | - | - | 7 | 0.44163 | 38.02 | 50.4329 | 15.3712 | 14.6498 | 14.6498 | 7.8415 | 0.0019673 | 0.0019635 | -0.0090842 | 0.0096039 | 0.14157
2549 | - | - | 7 | 0.44163 | 38.02 | 50.4644 | 15.3808 | 14.6594 | 14.6594 | 7.8435 | 0.0019635 | 0.0019596 | 0.0096039 | -0.0038921 | 1.4492
2554 | - | - | 7 | 0.44163 | 38.02 | 50.4517 | 15.3769 | 14.6555 | 14.6555 | 7.8454 | 0.0019596 | 0.0019558 | -0.0038921 | 0.0044961 | 0.15844
2559 | - | - | 7 | 0.44163 | 38.02 | 50.4664 | 15.3814 | 14.66 | 14.66 | 7.8474 | 0.0019558 | 0.001952 | 0.0044961 | 0.004902 | 2.4052
2564 | - | - | 7 | 0.44163 | 38.02 | 50.4825 | 15.3863 | 14.6649 | 14.6649 | 7.8493 | 0.001952 | 0.0019482 | 0.004902 | -0.0031921 | 0.43436
2569 | - | - | 7 | 0.44163 | 38.02 | 50.472 | 15.3831 | 14.6618 | 14.6618 | 7.8513 | 0.0019482 | 0.0019444 | -0.0031921 | 0.002902 | -0.071487 | 0.01545 | 0.015215 | 0.022953 | 0.016193 | 1.2733
2574 | - | - | 7 | 0.44163 | 38.02 | 50.4815 | 15.386 | 14.6647 | 14.6647 | 7.8532 | 0.0019444 | 0.0019406 | 0.002902 | 0.0173 | 5.2072
2579 | - | - | 7 | 0.44163 | 38.02 | 50.5383 | 15.4033 | 14.682 | 14.682 | 7.8552 | 0.0019406 | 0.0019369 | 0.0173 | 0.0023118 | 5.0504
2584 | - | - | 7 | 0.44163 | 38.02 | 50.5459 | 15.4056 | 14.6843 | 14.6843 | 7.8571 | 0.0019369 | 0.0019331 | 0.0023118 | 0.010492 | 3.3126
2589 | - | - | 7 | 0.44163 | 38.02 | 50.5803 | 15.4161 | 14.6948 | 14.6948 | 7.859 | 0.0019331 | 0.0019294 | 0.010492 | 0.005602 | 4.1643
2594 | - | - | 7 | 0.44163 | 38.02 | 50.5987 | 15.4217 | 14.7004 | 14.7004 | 7.861 | 0.0019294 | 0.0019257 | 0.005602 | -0.0083842 | -0.72871
2599 | - | - | 7 | 0.44163 | 38.02 | 50.5712 | 15.4133 | 14.692 | 14.692 | 7.8629 | 0.0019257 | 0.001922 | -0.0083842 | -0.0078822 | -4.2274
2604 | - | - | 7 | 0.44163 | 38.02 | 50.5453 | 15.4055 | 14.6841 | 14.6841 | 7.8648 | 0.001922 | 0.0019183 | -0.0078822 | 0.00061184 | -1.889
2609 | - | - | 7 | 0.44163 | 38.02 | 50.5473 | 15.4061 | 14.6847 | 14.6847 | 7.8667 | 0.0019183 | 0.0019146 | 0.00061184 | 0.011918 | 3.2746 | 0.015215 | 0.014987 | 0.016193 | 0.028561 | 1.4882
2614 | - | - | 7 | 0.44163 | 38.02 | 50.5864 | 15.418 | 14.6966 | 14.6966 | 7.8686 | 0.0019146 | 0.001911 | 0.011918 | -0.010294 | 0.41333
2619 | - | - | 7 | 0.44163 | 38.02 | 50.5527 | 15.4077 | 14.6863 | 14.6863 | 7.8705 | 0.001911 | 0.0019073 | -0.010294 | 0.0021059 | -2.1383
2624 | - | - | 7 | 0.44163 | 38.02 | 50.5596 | 15.4098 | 14.6884 | 14.6884 | 7.8725 | 0.0019073 | 0.0019037 | 0.0021059 | 0.0012197 | 0.87221
2629 | - | - | 7 | 0.44163 | 38.02 | 50.5636 | 15.411 | 14.6897 | 14.6897 | 7.8744 | 0.0019037 | 0.0019001 | 0.0012197 | -0.00049408 | 0.18992
2634 | - | - | 7 | 0.44163 | 38.02 | 50.562 | 15.4105 | 14.6892 | 14.6892 | 7.8763 | 0.0019001 | 0.0018965 | -0.00049408 | 0.01452 | 3.7019
2639 | - | - | 7 | 0.44163 | 38.02 | 50.6096 | 15.4251 | 14.7037 | 14.7037 | 7.8782 | 0.0018965 | 0.0018929 | 0.01452 | -0.0081842 | 1.6606
2644 | - | - | 7 | 0.44163 | 38.02 | 50.5827 | 15.4169 | 14.6955 | 14.6955 | 7.88 | 0.0018929 | 0.0018893 | -0.0081842 | 0.005402 | -0.72883
2649 | - | - | 7 | 0.44163 | 38.02 | 50.6005 | 15.4223 | 14.7009 | 14.7009 | 7.8819 | 0.0018893 | 0.0018857 | 0.005402 | 0.0097099 | 4.0053 | 0.014987 | 0.014766 | 0.028561 | 0.019055 | 1.5958
2654 | - | - | 7 | 0.44163 | 38.02 | 50.6323 | 15.432 | 14.7106 | 14.7106 | 7.8838 | 0.0018857 | 0.0018822 | 0.0097099 | -0.010102 | -0.11397
2659 | - | - | 7 | 0.44163 | 38.02 | 50.5992 | 15.4219 | 14.7005 | 14.7005 | 7.8857 | 0.0018822 | 0.0018786 | -0.010102 | 0.011394 | 0.35432
2664 | - | - | 7 | 0.44163 | 38.02 | 50.6366 | 15.4333 | 14.7119 | 14.7119 | 7.8876 | 0.0018786 | 0.0018751 | 0.011394 | 0.0078197 | 5.1168
2669 | - | - | 7 | 0.44163 | 38.02 | 50.6622 | 15.4411 | 14.7197 | 14.7197 | 7.8895 | 0.0018751 | 0.0018716 | 0.0078197 | 0.0003079 | 2.1655
2674 | - | - | 7 | 0.44163 | 38.02 | 50.6632 | 15.4414 | 14.72 | 14.72 | 7.8913 | 0.0018716 | 0.0018681 | 0.0003079 | -7.6312e-05 | 0.061733
2679 | - | - | 7 | 0.44163 | 38.02 | 50.663 | 15.4413 | 14.72 | 14.72 | 7.8932 | 0.0018681 | 0.0018646 | -7.6312e-05 | 0.0019079 | 0.49167
2684 | - | - | 7 | 0.44163 | 38.02 | 50.6692 | 15.4432 | 14.7219 | 14.7219 | 7.8951 | 0.0018646 | 0.0018612 | 0.0019079 | 0.0076 | 2.5548
2689 | - | - | 7 | 0.44163 | 38.02 | 50.6942 | 15.4508 | 14.7295 | 14.7295 | 7.8969 | 0.0018612 | 0.0018577 | 0.0076 | 0.0013099 | 2.3927 | 0.014766 | 0.014551 | 0.019055 | 0.049083 | 2.3395
2694 | - | - | 7 | 0.44163 | 38.02 | 50.6985 | 15.4521 | 14.7308 | 14.7308 | 7.8988 | 0.0018577 | 0.0018543 | 0.0013099 | 0.0045138 | 1.5705
2699 | - | - | 7 | 0.44163 | 38.02 | 50.7133 | 15.4567 | 14.7353 | 14.7353 | 7.9006 | 0.0018543 | 0.0018508 | 0.0045138 | 0.0052921 | 2.647
2704 | - | - | 7 | 0.44163 | 38.02 | 50.7306 | 15.4619 | 14.7406 | 14.7406 | 7.9025 | 0.0018508 | 0.0018474 | 0.0052921 | 0.0047 | 2.7016
2709 | - | - | 7 | 0.44163 | 38.02 | 50.7461 | 15.4666 | 14.7453 | 14.7453 | 7.9043 | 0.0018474 | 0.001844 | 0.0047 | -0.00018618 | 1.2204
2714 | - | - | 7 | 0.44163 | 38.02 | 50.7455 | 15.4665 | 14.7451 | 14.7451 | 7.9062 | 0.001844 | 0.0018406 | -0.00018618 | 0.0012039 | 0.27692
2719 | - | - | 7 | 0.44163 | 38.02 | 50.7494 | 15.4677 | 14.7463 | 14.7463 | 7.908 | 0.0018406 | 0.0018372 | 0.0012039 | 0.0031138 | 1.175
2724 | - | - | 7 | 0.44163 | 38.02 | 50.7596 | 15.4708 | 14.7494 | 14.7494 | 7.9099 | 0.0018372 | 0.0018339 | 0.0031138 | -0.0008921 | 0.60319
2729 | - | - | 7 | 0.44163 | 38.02 | 50.7567 | 15.4699 | 14.7485 | 14.7485 | 7.9117 | 0.0018339 | 0.0018305 | -0.0008921 | 0.0093901 | 2.3243 | 0.014551 | 0.014342 | 0.049083 | 0.088493 | 4.7817
2734 | - | - | 7 | 0.44163 | 38.02 | 50.7875 | 15.4793 | 14.7579 | 14.7579 | 7.9135 | 0.0018305 | 0.0018272 | 0.0093901 | 0.0064625 | 4.3326
2739 | - | - | 7 | 0.44163 | 38.02 | 50.8087 | 15.4857 | 14.7644 | 14.7644 | 7.9153 | 0.0018272 | 0.0018238 | 0.0064625 | 0.0080506 | 3.9759
2744 | - | - | 7 | 0.44163 | 38.02 | 50.8351 | 15.4938 | 14.7724 | 14.7724 | 7.9172 | 0.0018238 | 0.0018205 | 0.0080506 | -0.0016822 | 1.7426
2749 | - | - | 7 | 0.44163 | 38.02 | 50.8296 | 15.4921 | 14.7707 | 14.7707 | 7.919 | 0.0018205 | 0.0018172 | -0.0016822 | 0.013838 | 3.3492
2754 | - | - | 7 | 0.44163 | 38.02 | 50.875 | 15.5059 | 14.7846 | 14.7846 | 7.9208 | 0.0018172 | 0.0018139 | 0.013838 | -0.0012684 | 3.454
2759 | - | - | 7 | 0.44163 | 38.02 | 50.8708 | 15.5047 | 14.7833 | 14.7833 | 7.9226 | 0.0018139 | 0.0018106 | -0.0012684 | 0.0062375 | 1.3747
2764 | - | - | 7 | 0.44163 | 38.02 | 50.8913 | 15.5109 | 14.7895 | 14.7895 | 7.9244 | 0.0018106 | 0.0018073 | 0.0062375 | 0.0080553 | 3.9514
2769 | - | - | 7 | 0.44163 | 38.02 | 50.9177 | 15.519 | 14.7976 | 14.7976 | 7.9262 | 0.0018073 | 0.0018041 | 0.0080553 | 0.013708 | 6.0291 | 0.014342 | 0.01414 | 0.088493 | 0.039147 | 4.4572
2774 | - | - | 7 | 0.44163 | 38.02 | 50.9627 | 15.5327 | 14.8113 | 14.8113 | 7.928 | 0.0018041 | 0.0018008 | 0.013708 | -0.0052783 | 2.3289
2779 | - | - | 7 | 0.44163 | 38.02 | 50.9454 | 15.5274 | 14.806 | 14.806 | 7.9298 | 0.0018008 | 0.0017976 | -0.0052783 | 0.03511 | 8.3104
2784 | - | - | 7 | 0.44163 | 38.02 | 51.0606 | 15.5625 | 14.8411 | 14.8411 | 7.9316 | 0.0017976 | 0.0017944 | 0.03511 | 0.035926 | 19.7767
2789 | - | - | 7 | 0.44163 | 38.02 | 51.1785 | 15.5984 | 14.8771 | 14.8771 | 7.9334 | 0.0017944 | 0.0017912 | 0.035926 | 0.019804 | 15.5349
2794 | - | - | 7 | 0.44163 | 38.02 | 51.2434 | 15.6182 | 14.8969 | 14.8969 | 7.9352 | 0.0017912 | 0.0017879 | 0.019804 | 0.015202 | 9.7784
2799 | - | - | 7 | 0.44163 | 38.02 | 51.2933 | 15.6334 | 14.9121 | 14.9121 | 7.937 | 0.0017879 | 0.0017848 | 0.015202 | -0.029998 | -4.164
2804 | - | - | 7 | 0.44163 | 38.02 | 51.1949 | 15.6034 | 14.8821 | 14.8821 | 7.9388 | 0.0017848 | 0.0017816 | -0.029998 | 0.0040197 | -7.2673
2809 | - | - | 7 | 0.44163 | 38.02 | 51.2081 | 15.6075 | 14.8861 | 14.8861 | 7.9406 | 0.0017816 | 0.0017784 | 0.0040197 | 0.016318 | 5.719 | 0.01414 | 0.013942 | 0.039147 | 0.05302 | 3.2893
2814 | - | - | 7 | 0.44163 | 38.02 | 51.2616 | 15.6238 | 14.9024 | 14.9024 | 7.9424 | 0.0017784 | 0.0017753 | 0.016318 | 0.01211 | 7.9974
2819 | - | - | 7 | 0.44163 | 38.02 | 51.3014 | 15.6359 | 14.9145 | 14.9145 | 7.9441 | 0.0017753 | 0.0017721 | 0.01211 | 0.0082941 | 5.75
2824 | - | - | 7 | 0.44163 | 38.02 | 51.3286 | 15.6442 | 14.9228 | 14.9228 | 7.9459 | 0.0017721 | 0.001769 | 0.0082941 | 0.0021118 | 2.9355
2829 | - | - | 7 | 0.44163 | 38.02 | 51.3355 | 15.6463 | 14.9249 | 14.9249 | 7.9477 | 0.001769 | 0.0017658 | 0.0021118 | -0.00068816 | 0.40136
2834 | - | - | 7 | 0.44163 | 38.02 | 51.3332 | 15.6456 | 14.9242 | 14.9242 | 7.9494 | 0.0017658 | 0.0017627 | -0.00068816 | 0.017239 | 4.6996
2839 | - | - | 7 | 0.44163 | 38.02 | 51.3898 | 15.6628 | 14.9415 | 14.9415 | 7.9512 | 0.0017627 | 0.0017596 | 0.017239 | -0.013241 | 1.1198
2844 | - | - | 7 | 0.44163 | 38.02 | 51.3464 | 15.6496 | 14.9282 | 14.9282 | 7.953 | 0.0017596 | 0.0017565 | -0.013241 | -0.0029961 | -4.6128
2849 | - | - | 7 | 0.44163 | 38.02 | 51.3365 | 15.6466 | 14.9252 | 14.9252 | 7.9547 | 0.0017565 | 0.0017535 | -0.0029961 | 0.007798 | 1.3735 | 0.013942 | 0.013751 | 0.05302 | 0.0056033 | 2.0934
2854 | - | - | 7 | 0.44163 | 38.02 | 51.3621 | 15.6544 | 14.933 | 14.933 | 7.9565 | 0.0017535 | 0.0017504 | 0.007798 | 0.0031237 | 3.1147
2859 | - | - | 7 | 0.44163 | 38.02 | 51.3724 | 15.6575 | 14.9362 | 14.9362 | 7.9582 | 0.0017504 | 0.0017473 | 0.0031237 | 0.0041664 | 2.0848
2864 | - | - | 7 | 0.44163 | 38.02 | 51.386 | 15.6617 | 14.9403 | 14.9403 | 7.96 | 0.0017473 | 0.0017443 | 0.0041664 | -0.0015822 | 0.73724
2869 | - | - | 7 | 0.44163 | 38.02 | 51.3808 | 15.6601 | 14.9387 | 14.9387 | 7.9617 | 0.0017443 | 0.0017413 | -0.0015822 | 0.0096099 | 2.3087
2874 | - | - | 7 | 0.44163 | 38.02 | 51.4124 | 15.6697 | 14.9484 | 14.9484 | 7.9635 | 0.0017413 | 0.0017382 | 0.0096099 | 0.0082822 | 5.1415
2879 | - | - | 7 | 0.44163 | 38.02 | 51.4395 | 15.678 | 14.9566 | 14.9566 | 7.9652 | 0.0017382 | 0.0017352 | 0.0082822 | 0.0081237 | 4.7232
2884 | - | - | 7 | 0.44163 | 38.02 | 51.4662 | 15.6861 | 14.9648 | 14.9648 | 7.9669 | 0.0017352 | 0.0017322 | 0.0081237 | 0.013498 | 6.2384
2889 | - | - | 7 | 0.44163 | 38.02 | 51.5105 | 15.6996 | 14.9783 | 14.9783 | 7.9687 | 0.0017322 | 0.0017292 | 0.013498 | 0.0023079 | 4.5607 | 0.013751 | 0.013564 | 0.0056033 | 0.032896 | 1.4232
2894 | - | - | 7 | 0.44163 | 38.02 | 51.5181 | 15.7019 | 14.9806 | 14.9806 | 7.9704 | 0.0017292 | 0.0017262 | 0.0023079 | 0.010412 | 3.6851
2899 | - | - | 7 | 0.44163 | 38.02 | 51.5522 | 15.7123 | 14.991 | 14.991 | 7.9721 | 0.0017262 | 0.0017232 | 0.010412 | -0.0070961 | 0.95249
2904 | - | - | 7 | 0.44163 | 38.02 | 51.5289 | 15.7053 | 14.9839 | 14.9839 | 7.9738 | 0.0017232 | 0.0017203 | -0.0070961 | -0.0039197 | -3.1974
2909 | - | - | 7 | 0.44163 | 38.02 | 51.5161 | 15.7013 | 14.98 | 14.98 | 7.9756 | 0.0017203 | 0.0017173 | -0.0039197 | 0.0078605 | 1.1523
2914 | - | - | 7 | 0.44163 | 38.02 | 51.5419 | 15.7092 | 14.9878 | 14.9878 | 7.9773 | 0.0017173 | 0.0017144 | 0.0078605 | 0.0015783 | 2.7473
2919 | - | - | 7 | 0.44163 | 38.02 | 51.547 | 15.7108 | 14.9894 | 14.9894 | 7.979 | 0.0017144 | 0.0017115 | 0.0015783 | 0.0038763 | 1.5933
2924 | - | - | 7 | 0.44163 | 38.02 | 51.5598 | 15.7146 | 14.9933 | 14.9933 | 7.9807 | 0.0017115 | 0.0017085 | 0.0038763 | -0.0094158 | -1.6264
2929 | - | - | 7 | 0.44163 | 38.02 | 51.5289 | 15.7052 | 14.9839 | 14.9839 | 7.9824 | 0.0017085 | 0.0017056 | -0.0094158 | -0.0021197 | -3.3751 | 0.013564 | 0.013383 | 0.032896 | 0.011066 | 1.6207
2934 | - | - | 7 | 0.44163 | 38.02 | 51.5219 | 15.7031 | 14.9817 | 14.9817 | 7.9841 | 0.0017056 | 0.0017027 | -0.0021197 | 0.013408 | 3.3197
2939 | - | - | 7 | 0.44163 | 38.02 | 51.5659 | 15.7165 | 14.9952 | 14.9952 | 7.9858 | 0.0017027 | 0.0016998 | 0.013408 | -0.0061355 | 2.1276
2944 | - | - | 7 | 0.44163 | 38.02 | 51.5458 | 15.7104 | 14.989 | 14.989 | 7.9875 | 0.0016998 | 0.0016969 | -0.0061355 | 0.0029375 | -0.93696
2949 | - | - | 7 | 0.44163 | 38.02 | 51.5554 | 15.7133 | 14.992 | 14.992 | 7.9892 | 0.0016969 | 0.0016941 | 0.0029375 | 0.0080099 | 3.2309
2954 | - | - | 7 | 0.44163 | 38.02 | 51.5817 | 15.7213 | 15 | 15 | 7.9909 | 0.0016941 | 0.0016912 | 0.0080099 | 0.010322 | 5.4163
2959 | - | - | 7 | 0.44163 | 38.02 | 51.6156 | 15.7317 | 15.0103 | 15.0103 | 7.9926 | 0.0016912 | 0.0016883 | 0.010322 | 0.0034316 | 4.0662
2964 | - | - | 7 | 0.44163 | 38.02 | 51.6268 | 15.7351 | 15.0137 | 15.0137 | 7.9943 | 0.0016883 | 0.0016855 | 0.0034316 | 0.0030428 | 1.9188
2969 | - | - | 7 | 0.44163 | 38.02 | 51.6368 | 15.7381 | 15.0168 | 15.0168 | 7.996 | 0.0016855 | 0.0016827 | 0.0030428 | -0.00093553 | 0.62365 | 0.013383 | 0.013206 | 0.011066 | 0.026227 | 1.4103
2974 | - | - | 7 | 0.44163 | 38.02 | 51.6337 | 15.7372 | 15.0158 | 15.0158 | 7.9977 | 0.0016827 | 0.0016798 | -0.00093553 | -0.0020408 | -0.88571
2979 | - | - | 7 | 0.44163 | 38.02 | 51.627 | 15.7352 | 15.0138 | 15.0138 | 7.9993 | 0.0016798 | 0.001677 | -0.0020408 | -0.0016809 | -1.1085
2984 | - | - | 7 | 0.44163 | 38.02 | 51.6215 | 15.7335 | 15.0121 | 15.0121 | 8.001 | 0.001677 | 0.0016742 | -0.0016809 | 0.0069901 | 1.5886
2989 | - | - | 7 | 0.44163 | 38.02 | 51.6445 | 15.7405 | 15.0191 | 15.0191 | 8.0027 | 0.0016742 | 0.0016714 | 0.0069901 | 0.0071961 | 4.2404
2994 | - | - | 7 | 0.44163 | 38.02 | 51.6681 | 15.7477 | 15.0263 | 15.0263 | 8.0044 | 0.0016714 | 0.0016686 | 0.0071961 | -0.012547 | -1.6121
2999 | - | - | 7 | 0.44163 | 38.02 | 51.6269 | 15.7351 | 15.0137 | 15.0137 | 8.006 | 0.0016686 | 0.0016658 | -0.012547 | 0.021084 | 2.577
3004 | - | - | 7 | 0.44163 | 38.02 | 51.6961 | 15.7562 | 15.0348 | 15.0348 | 8.0077 | 0.0016658 | 0.0016631 | 0.021084 | -0.007 | 4.2169
3009 | - | - | 7 | 0.44163 | 38.02 | 51.6731 | 15.7492 | 15.0278 | 15.0278 | 8.0094 | 0.0016631 | 0.0016603 | -0.007 | 0.0047842 | -0.66084 | 0.013206 | 0.013034 | 0.026227 | 0.023843 | 1.9071
3014 | - | - | 7 | 0.44163 | 38.02 | 51.6888 | 15.754 | 15.0326 | 15.0326 | 8.011 | 0.0016603 | 0.0016576 | 0.0047842 | 0.003098 | 2.3749
3019 | - | - | 7 | 0.44163 | 38.02 | 51.699 | 15.7571 | 15.0357 | 15.0357 | 8.0127 | 0.0016576 | 0.0016548 | 0.003098 | 0.0072783 | 3.1347
3024 | - | - | 7 | 0.44163 | 38.02 | 51.7228 | 15.7644 | 15.043 | 15.043 | 8.0143 | 0.0016548 | 0.0016521 | 0.0072783 | -0.010298 | -0.92196
3029 | - | - | 7 | 0.44163 | 38.02 | 51.6891 | 15.7541 | 15.0327 | 15.0327 | 8.016 | 0.0016521 | 0.0016493 | -0.010298 | 0.011076 | 0.24643
3034 | - | - | 7 | 0.44163 | 38.02 | 51.7254 | 15.7651 | 15.0438 | 15.0438 | 8.0176 | 0.0016493 | 0.0016466 | 0.011076 | 0.0020039 | 3.964
3039 | - | - | 7 | 0.44163 | 38.02 | 51.732 | 15.7671 | 15.0458 | 15.0458 | 8.0193 | 0.0016466 | 0.0016439 | 0.0020039 | 0.007302 | 2.8307
3044 | - | - | 7 | 0.44163 | 38.02 | 51.7559 | 15.7744 | 15.0531 | 15.0531 | 8.0209 | 0.0016439 | 0.0016412 | 0.007302 | 0.00098223 | 2.5186
3049 | - | - | 7 | 0.44163 | 38.02 | 51.7592 | 15.7754 | 15.0541 | 15.0541 | 8.0226 | 0.0016412 | 0.0016385 | 0.00098223 | -0.0025059 | -0.46632 | 0.013034 | 0.012866 | 0.023843 | -0.085605 | -2.4396
3054 | - | - | 7 | 0.44163 | 38.02 | 51.7509 | 15.7729 | 15.0515 | 15.0515 | 8.0242 | 0.0016385 | 0.0016359 | -0.0025059 | 0.0101 | 2.3255
3059 | - | - | 7 | 0.44163 | 38.02 | 51.7841 | 15.783 | 15.0616 | 15.0616 | 8.0258 | 0.0016359 | 0.0016332 | 0.0101 | -0.0098118 | 0.078191
3064 | - | - | 7 | 0.44163 | 38.02 | 51.7519 | 15.7732 | 15.0518 | 15.0518 | 8.0275 | 0.0016332 | 0.0016305 | -0.0098118 | 0.010792 | 0.31065
3069 | - | - | 7 | 0.44163 | 38.02 | 51.7873 | 15.784 | 15.0626 | 15.0626 | 8.0291 | 0.0016305 | 0.0016279 | 0.010792 | 0.002298 | 4.0131
3074 | - | - | 7 | 0.44163 | 38.02 | 51.7948 | 15.7863 | 15.0649 | 15.0649 | 8.0307 | 0.0016279 | 0.0016252 | 0.002298 | 0.0020961 | 1.3506
3079 | - | - | 7 | 0.44163 | 38.02 | 51.8017 | 15.7884 | 15.067 | 15.067 | 8.0324 | 0.0016252 | 0.0016226 | 0.0020961 | 0.0065724 | 2.6712
3084 | - | - | 7 | 0.44163 | 38.02 | 51.8233 | 15.795 | 15.0736 | 15.0736 | 8.034 | 0.0016226 | 0.00162 | 0.0065724 | 0.004302 | 3.3525
3089 | - | - | 7 | 0.44163 | 38.02 | 51.8374 | 15.7993 | 15.0779 | 15.0779 | 8.0356 | 0.00162 | 0.0016173 | 0.004302 | -0.038532 | -10.5949 | 0.012866 | 0.012703 | -0.085605 | 0.098831 | 0.60955
3094 | - | - | 7 | 0.44163 | 38.02 | 51.711 | 15.7607 | 15.0394 | 15.0394 | 8.0372 | 0.0016173 | 0.0016147 | -0.038532 | -0.021004 | -18.4115
3099 | - | - | 7 | 0.44163 | 38.02 | 51.642 | 15.7397 | 15.0184 | 15.0184 | 8.0388 | 0.0016147 | 0.0016121 | -0.021004 | -0.0039039 | -7.7104
3104 | - | - | 7 | 0.44163 | 38.02 | 51.6292 | 15.7358 | 15.0145 | 15.0145 | 8.0404 | 0.0016121 | 0.0016095 | -0.0039039 | -0.0054257 | -2.8967
3109 | - | - | 7 | 0.44163 | 38.02 | 51.6114 | 15.7304 | 15.009 | 15.009 | 8.0421 | 0.0016095 | 0.0016069 | -0.0054257 | -0.0010961 | -2.0254
3114 | - | - | 7 | 0.44163 | 38.02 | 51.6078 | 15.7293 | 15.0079 | 15.0079 | 8.0437 | 0.0016069 | 0.0016044 | -0.0010961 | -0.0021237 | -1.0031
3119 | - | - | 7 | 0.44163 | 38.02 | 51.6009 | 15.7272 | 15.0058 | 15.0058 | 8.0453 | 0.0016044 | 0.0016018 | -0.0021237 | -0.015214 | -5.4141
3124 | - | - | 7 | 0.44163 | 38.02 | 51.551 | 15.712 | 14.9906 | 14.9906 | 8.0469 | 0.0016018 | 0.0015992 | -0.015214 | 0.0016941 | -4.2151
3129 | - | - | 7 | 0.44163 | 38.02 | 51.5565 | 15.7137 | 14.9923 | 14.9923 | 8.0485 | 0.0015992 | 0.0015967 | 0.0016941 | 0.0022 | 1.2187 | 0.012703 | 0.012543 | 0.098831 | 0.01437 | 4.4421
3134 | - | - | 7 | 0.44163 | 38.02 | 51.5637 | 15.7159 | 14.9945 | 14.9945 | 8.0501 | 0.0015967 | 0.0015941 | 0.0022 | 0.0033783 | 1.7488
3139 | - | - | 7 | 0.44163 | 38.02 | 51.5748 | 15.7192 | 14.9979 | 14.9979 | 8.0517 | 0.0015941 | 0.0015916 | 0.0033783 | 0.0013039 | 1.4687
3144 | - | - | 7 | 0.44163 | 38.02 | 51.5791 | 15.7205 | 14.9992 | 14.9992 | 8.0533 | 0.0015916 | 0.0015891 | 0.0013039 | 0.040596 | 13.193
3149 | - | - | 7 | 0.44163 | 38.02 | 51.7123 | 15.7611 | 15.0398 | 15.0398 | 8.0548 | 0.0015891 | 0.0015865 | 0.040596 | 0.027798 | 21.5309
3154 | - | - | 7 | 0.44163 | 38.02 | 51.8035 | 15.7889 | 15.0676 | 15.0676 | 8.0564 | 0.0015865 | 0.001584 | 0.027798 | 0.01248 | 12.6961
3159 | - | - | 7 | 0.44163 | 38.02 | 51.8444 | 15.8014 | 15.08 | 15.08 | 8.058 | 0.001584 | 0.0015815 | 0.01248 | 9.013e-05 | 3.9648
3164 | - | - | 7 | 0.44163 | 38.02 | 51.8447 | 15.8015 | 15.0801 | 15.0801 | 8.0596 | 0.0015815 | 0.001579 | 9.013e-05 | 0.010984 | 3.5094
3169 | - | - | 7 | 0.44163 | 38.02 | 51.8808 | 15.8125 | 15.0911 | 15.0911 | 8.0612 | 0.001579 | 0.0015765 | 0.010984 | 0.010804 | 6.9046 | 0.012543 | 0.012388 | 0.01437 | 0.011249 | 1.0261
3174 | - | - | 7 | 0.44163 | 38.02 | 51.9162 | 15.8233 | 15.1019 | 15.1019 | 8.0627 | 0.0015765 | 0.0015741 | 0.010804 | -0.0017197 | 2.8771
3179 | - | - | 7 | 0.44163 | 38.02 | 51.9106 | 15.8216 | 15.1002 | 15.1002 | 8.0643 | 0.0015741 | 0.0015716 | -0.0017197 | -0.002198 | -1.2457
3184 | - | - | 7 | 0.44163 | 38.02 | 51.9034 | 15.8194 | 15.098 | 15.098 | 8.0659 | 0.0015716 | 0.0015691 | -0.002198 | 0.0050842 | 0.9226
3189 | - | - | 7 | 0.44163 | 38.02 | 51.9201 | 15.8245 | 15.1031 | 15.1031 | 8.0675 | 0.0015691 | 0.0015667 | 0.0050842 | 0.0072118 | 3.9223
3194 | - | - | 7 | 0.44163 | 38.02 | 51.9437 | 15.8317 | 15.1103 | 15.1103 | 8.069 | 0.0015667 | 0.0015642 | 0.0072118 | -0.0027941 | 1.406
3199 | - | - | 7 | 0.44163 | 38.02 | 51.9345 | 15.8289 | 15.1075 | 15.1075 | 8.0706 | 0.0015642 | 0.0015618 | -0.0027941 | -0.0054138 | -2.627
3204 | - | - | 7 | 0.44163 | 38.02 | 51.9168 | 15.8235 | 15.1021 | 15.1021 | 8.0722 | 0.0015618 | 0.0015593 | -0.0054138 | 0.0033961 | -0.64209
3209 | - | - | 7 | 0.44163 | 38.02 | 51.9279 | 15.8269 | 15.1055 | 15.1055 | 8.0737 | 0.0015593 | 0.0015569 | 0.0033961 | 0.0094 | 4.1093 | 0.012388 | 0.012236 | 0.011249 | 0.027527 | 1.583
3214 | - | - | 7 | 0.44163 | 38.02 | 51.9588 | 15.8363 | 15.1149 | 15.1149 | 8.0753 | 0.0015569 | 0.0015545 | 0.0094 | -0.0029237 | 2.0753
3219 | - | - | 7 | 0.44163 | 38.02 | 51.9492 | 15.8333 | 15.112 | 15.112 | 8.0768 | 0.0015545 | 0.0015521 | -0.0029237 | -0.00020395 | -1.0054
3224 | - | - | 7 | 0.44163 | 38.02 | 51.9485 | 15.8331 | 15.1118 | 15.1118 | 8.0784 | 0.0015521 | 0.0015497 | -0.00020395 | -0.0021059 | -0.74565
3229 | - | - | 7 | 0.44163 | 38.02 | 51.9416 | 15.831 | 15.1097 | 15.1097 | 8.0799 | 0.0015497 | 0.0015473 | -0.0021059 | 0.0060803 | 1.2874
3234 | - | - | 7 | 0.44163 | 38.02 | 51.9615 | 15.8371 | 15.1157 | 15.1157 | 8.0815 | 0.0015473 | 0.0015449 | 0.0060803 | 0.00070592 | 2.192
3239 | - | - | 7 | 0.44163 | 38.02 | 51.9639 | 15.8378 | 15.1164 | 15.1164 | 8.083 | 0.0015449 | 0.0015425 | 0.00070592 | 0.00030592 | 0.32754
3244 | - | - | 7 | 0.44163 | 38.02 | 51.9649 | 15.8381 | 15.1167 | 15.1167 | 8.0846 | 0.0015425 | 0.0015401 | 0.00030592 | -9.87e-06 | 0.095881
3249 | - | - | 7 | 0.44163 | 38.02 | 51.9648 | 15.8381 | 15.1167 | 15.1167 | 8.0861 | 0.0015401 | 0.0015378 | -9.87e-06 | 0.015298 | 4.9748 | 0.012236 | 0.012088 | 0.027527 | 0.016164 | 1.7906
3254 | - | - | 7 | 0.44163 | 38.02 | 52.015 | 15.8534 | 15.132 | 15.132 | 8.0876 | 0.0015378 | 0.0015354 | 0.015298 | -0.012126 | 1.0186
3259 | - | - | 7 | 0.44163 | 38.02 | 51.9752 | 15.8413 | 15.1199 | 15.1199 | 8.0892 | 0.0015354 | 0.001533 | -0.012126 | 0.006802 | -1.7255
3264 | - | - | 7 | 0.44163 | 38.02 | 51.9976 | 15.8481 | 15.1267 | 15.1267 | 8.0907 | 0.001533 | 0.0015307 | 0.006802 | -0.0012138 | 1.82
3269 | - | - | 7 | 0.44163 | 38.02 | 51.9936 | 15.8469 | 15.1255 | 15.1255 | 8.0922 | 0.0015307 | 0.0015284 | -0.0012138 | 0.0064941 | 1.73
3274 | - | - | 7 | 0.44163 | 38.02 | 52.0149 | 15.8534 | 15.132 | 15.132 | 8.0938 | 0.0015284 | 0.001526 | 0.0064941 | 0.0024822 | 2.9368
3279 | - | - | 7 | 0.44163 | 38.02 | 52.023 | 15.8558 | 15.1345 | 15.1345 | 8.0953 | 0.001526 | 0.0015237 | 0.0024822 | 0.007498 | 3.275
3284 | - | - | 7 | 0.44163 | 38.02 | 52.0476 | 15.8633 | 15.142 | 15.142 | 8.0968 | 0.0015237 | 0.0015214 | 0.007498 | 0.0022921 | 3.2125
3289 | - | - | 7 | 0.44163 | 38.02 | 52.0552 | 15.8656 | 15.1443 | 15.1443 | 8.0983 | 0.0015214 | 0.0015191 | 0.0022921 | 0.0071099 | 3.0947 | 0.012088 | 0.011944 | 0.016164 | -0.00061382 | 0.63873
3294 | - | - | 7 | 0.44163 | 38.02 | 52.0785 | 15.8727 | 15.1514 | 15.1514 | 8.0999 | 0.0015191 | 0.0015168 | 0.0071099 | -0.011724 | -1.5292
3299 | - | - | 7 | 0.44163 | 38.02 | 52.04 | 15.861 | 15.1397 | 15.1397 | 8.1014 | 0.0015168 | 0.0015145 | -0.011724 | 0.0096901 | -0.66016
3304 | - | - | 7 | 0.44163 | 38.02 | 52.0718 | 15.8707 | 15.1493 | 15.1493 | 8.1029 | 0.0015145 | 0.0015122 | 0.0096901 | -0.0019118 | 2.5641
3309 | - | - | 7 | 0.44163 | 38.02 | 52.0655 | 15.8688 | 15.1474 | 15.1474 | 8.1044 | 0.0015122 | 0.0015099 | -0.0019118 | 0.007398 | 1.82
3314 | - | - | 7 | 0.44163 | 38.02 | 52.0898 | 15.8762 | 15.1548 | 15.1548 | 8.1059 | 0.0015099 | 0.0015076 | 0.007398 | -0.0022039 | 1.7165
3319 | - | - | 7 | 0.44163 | 38.02 | 52.0826 | 15.874 | 15.1526 | 15.1526 | 8.1074 | 0.0015076 | 0.0015053 | -0.0022039 | -0.005198 | -2.4582
3324 | - | - | 7 | 0.44163 | 38.02 | 52.0655 | 15.8688 | 15.1474 | 15.1474 | 8.1089 | 0.0015053 | 0.0015031 | -0.005198 | 0.013004 | 2.6038
3329 | - | - | 7 | 0.44163 | 38.02 | 52.1082 | 15.8818 | 15.1604 | 15.1604 | 8.1104 | 0.0015031 | 0.0015008 | 0.013004 | -0.0025039 | 3.4877 | 0.011944 | 0.011803 | -0.00061382 | 0.022706 | 0.94204
3334 | - | - | 7 | 0.44163 | 38.02 | 52.1 | 15.8793 | 15.1579 | 15.1579 | 8.1119 | 0.0015008 | 0.0014986 | -0.0025039 | -0.0026079 | -1.7043
3339 | - | - | 7 | 0.44163 | 38.02 | 52.0914 | 15.8767 | 15.1553 | 15.1553 | 8.1134 | 0.0014986 | 0.0014963 | -0.0026079 | 0.0012039 | -0.46687
3344 | - | - | 7 | 0.44163 | 38.02 | 52.0954 | 15.8779 | 15.1565 | 15.1565 | 8.1149 | 0.0014963 | 0.0014941 | 0.0012039 | -0.0031039 | -0.63751
3349 | - | - | 7 | 0.44163 | 38.02 | 52.0852 | 15.8748 | 15.1534 | 15.1534 | 8.1164 | 0.0014941 | 0.0014919 | -0.0031039 | 0.007502 | 1.4782
3354 | - | - | 7 | 0.44163 | 38.02 | 52.1098 | 15.8823 | 15.1609 | 15.1609 | 8.1179 | 0.0014919 | 0.0014896 | 0.007502 | -0.002002 | 1.8399
3359 | - | - | 7 | 0.44163 | 38.02 | 52.1032 | 15.8803 | 15.1589 | 15.1589 | 8.1194 | 0.0014896 | 0.0014874 | -0.002002 | 0.0012862 | -0.23879
3364 | - | - | 7 | 0.44163 | 38.02 | 52.1074 | 15.8816 | 15.1602 | 15.1602 | 8.1209 | 0.0014874 | 0.0014852 | 0.0012862 | -0.00038816 | 0.30126
3369 | - | - | 7 | 0.44163 | 38.02 | 52.1062 | 15.8812 | 15.1598 | 15.1598 | 8.1224 | 0.0014852 | 0.001483 | -0.00038816 | 0.0043079 | 1.3229 | 0.011803 | 0.011665 | 0.022706 | 0.014547 | 1.5834
3374 | - | - | 7 | 0.44163 | 38.02 | 52.1203 | 15.8855 | 15.1641 | 15.1641 | 8.1239 | 0.001483 | 0.0014808 | 0.0043079 | 0.012806 | 5.7785
3379 | - | - | 7 | 0.44163 | 38.02 | 52.1623 | 15.8983 | 15.1769 | 15.1769 | 8.1253 | 0.0014808 | 0.0014786 | 0.012806 | 0.0015921 | 4.8595
3384 | - | - | 7 | 0.44163 | 38.02 | 52.1675 | 15.8999 | 15.1785 | 15.1785 | 8.1268 | 0.0014786 | 0.0014765 | 0.0015921 | -0.0055 | -1.326
3389 | - | - | 7 | 0.44163 | 38.02 | 52.1495 | 15.8944 | 15.173 | 15.173 | 8.1283 | 0.0014765 | 0.0014743 | -0.0055 | 0.009898 | 1.4982
3394 | - | - | 7 | 0.44163 | 38.02 | 52.182 | 15.9043 | 15.1829 | 15.1829 | 8.1298 | 0.0014743 | 0.0014721 | 0.009898 | -0.0022 | 2.6067
3399 | - | - | 7 | 0.44163 | 38.02 | 52.1748 | 15.9021 | 15.1807 | 15.1807 | 8.1312 | 0.0014721 | 0.0014699 | -0.0022 | -0.0024059 | -1.5657
3404 | - | - | 7 | 0.44163 | 38.02 | 52.1669 | 15.8997 | 15.1783 | 15.1783 | 8.1327 | 0.0014699 | 0.0014678 | -0.0024059 | 0.0042079 | 0.6167
3409 | - | - | 7 | 0.44163 | 38.02 | 52.1807 | 15.9039 | 15.1825 | 15.1825 | 8.1342 | 0.0014678 | 0.0014656 | 0.0042079 | 0.0074079 | 3.9614 | 0.011665 | 0.011531 | 0.014547 | 0.011843 | 1.1364
3414 | - | - | 7 | 0.44163 | 38.02 | 52.205 | 15.9113 | 15.1899 | 15.1899 | 8.1356 | 0.0014656 | 0.0014635 | 0.0074079 | -0.00099803 | 2.1841
3419 | - | - | 7 | 0.44163 | 38.02 | 52.2017 | 15.9103 | 15.1889 | 15.1889 | 8.1371 | 0.0014635 | 0.0014613 | -0.00099803 | -0.00049605 | -0.51057
3424 | - | - | 7 | 0.44163 | 38.02 | 52.2001 | 15.9098 | 15.1884 | 15.1884 | 8.1386 | 0.0014613 | 0.0014592 | -0.00049605 | 0.0048039 | 1.4777
3429 | - | - | 7 | 0.44163 | 38.02 | 52.2158 | 15.9146 | 15.1932 | 15.1932 | 8.14 | 0.0014592 | 0.0014571 | 0.0048039 | -0.002298 | 0.85573
3434 | - | - | 7 | 0.44163 | 38.02 | 52.2083 | 15.9123 | 15.1909 | 15.1909 | 8.1415 | 0.0014571 | 0.001455 | -0.002298 | 0.013612 | 3.8931
3439 | - | - | 7 | 0.44163 | 38.02 | 52.253 | 15.9259 | 15.2046 | 15.2046 | 8.1429 | 0.001455 | 0.0014529 | 0.013612 | -0.0040862 | 3.267
3444 | - | - | 7 | 0.44163 | 38.02 | 52.2395 | 15.9218 | 15.2005 | 15.2005 | 8.1444 | 0.0014529 | 0.0014507 | -0.0040862 | -0.003398 | -2.5772
3449 | - | - | 7 | 0.44163 | 38.02 | 52.2284 | 15.9184 | 15.1971 | 15.1971 | 8.1458 | 0.0014507 | 0.0014486 | -0.003398 | -0.0012 | -1.5848 | 0.011531 | 0.011399 | 0.011843 | 0.025259 | 1.6249
3454 | - | - | 7 | 0.44163 | 38.02 | 52.2245 | 15.9172 | 15.1959 | 15.1959 | 8.1473 | 0.0014486 | 0.0014466 | -0.0012 | 0.0023059 | 0.38374
3459 | - | - | 7 | 0.44163 | 38.02 | 52.232 | 15.9195 | 15.1982 | 15.1982 | 8.1487 | 0.0014466 | 0.0014445 | 0.0023059 | 0.010422 | 4.4065
3464 | - | - | 7 | 0.44163 | 38.02 | 52.2662 | 15.93 | 15.2086 | 15.2086 | 8.1502 | 0.0014445 | 0.0014424 | 0.010422 | 0.0030118 | 4.6497
3469 | - | - | 7 | 0.44163 | 38.02 | 52.2761 | 15.933 | 15.2116 | 15.2116 | 8.1516 | 0.0014424 | 0.0014403 | 0.0030118 | -0.0059862 | -1.0363
3474 | - | - | 7 | 0.44163 | 38.02 | 52.2565 | 15.927 | 15.2056 | 15.2056 | 8.1531 | 0.0014403 | 0.0014382 | -0.0059862 | -0.0048039 | -3.7479
3479 | - | - | 7 | 0.44163 | 38.02 | 52.2407 | 15.9222 | 15.2008 | 15.2008 | 8.1545 | 0.0014382 | 0.0014362 | -0.0048039 | 0.0049079 | 0.041019
3484 | - | - | 7 | 0.44163 | 38.02 | 52.2568 | 15.9271 | 15.2057 | 15.2057 | 8.1559 | 0.0014362 | 0.0014341 | 0.0049079 | 0.0031862 | 2.8191
3489 | - | - | 7 | 0.44163 | 38.02 | 52.2673 | 15.9303 | 15.2089 | 15.2089 | 8.1574 | 0.0014341 | 0.001432 | 0.0031862 | 0.0062921 | 3.3085 | 0.011399 | 0.011271 | 0.025259 | 0.011839 | 1.6298
3494 | - | - | 7 | 0.44163 | 38.02 | 52.2879 | 15.9366 | 15.2152 | 15.2152 | 8.1588 | 0.001432 | 0.00143 | 0.0062921 | 0.0068217 | 4.5822
3499 | - | - | 7 | 0.44163 | 38.02 | 52.3103 | 15.9434 | 15.222 | 15.222 | 8.1602 | 0.00143 | 0.001428 | 0.0068217 | -0.0064921 | 0.10867
3504 | - | - | 7 | 0.44163 | 38.02 | 52.289 | 15.9369 | 15.2155 | 15.2155 | 8.1617 | 0.001428 | 0.0014259 | -0.0064921 | 0.0014862 | -1.7501
3509 | - | - | 7 | 0.44163 | 38.02 | 52.2939 | 15.9384 | 15.217 | 15.217 | 8.1631 | 0.0014259 | 0.0014239 | 0.0014862 | 0.0086099 | 3.5463
3514 | - | - | 7 | 0.44163 | 38.02 | 52.3221 | 15.947 | 15.2256 | 15.2256 | 8.1645 | 0.0014239 | 0.0014219 | 0.0086099 | 1.1844e-05 | 3.0254
3519 | - | - | 7 | 0.44163 | 38.02 | 52.3221 | 15.947 | 15.2256 | 15.2256 | 8.1659 | 0.0014219 | 0.0014198 | 1.1844e-05 | -0.0042901 | -1.5077
3524 | - | - | 7 | 0.44163 | 38.02 | 52.3081 | 15.9427 | 15.2214 | 15.2214 | 8.1674 | 0.0014198 | 0.0014178 | -0.0042901 | 0.01282 | 3.0144
3529 | - | - | 7 | 0.44163 | 38.02 | 52.3501 | 15.9555 | 15.2342 | 15.2342 | 8.1688 | 0.0014178 | 0.0014158 | 0.01282 | 0.0016099 | 5.0866 | 0.011271 | 0.011145 | 0.011839 | 0.028002 | 1.7855
3534 | - | - | 7 | 0.44163 | 38.02 | 52.3554 | 15.9572 | 15.2358 | 15.2358 | 8.1702 | 0.0014158 | 0.0014138 | 0.0016099 | 0.0034079 | 1.7742
3539 | - | - | 7 | 0.44163 | 38.02 | 52.3666 | 15.9606 | 15.2392 | 15.2392 | 8.1716 | 0.0014138 | 0.0014118 | 0.0034079 | 0.0043099 | 2.7318
3544 | - | - | 7 | 0.44163 | 38.02 | 52.3807 | 15.9649 | 15.2435 | 15.2435 | 8.173 | 0.0014118 | 0.0014098 | 0.0043099 | -0.0085961 | -1.5255
3549 | - | - | 7 | 0.44163 | 38.02 | 52.3525 | 15.9563 | 15.2349 | 15.2349 | 8.1744 | 0.0014098 | 0.0014079 | -0.0085961 | 0.01802 | 3.3578
3554 | - | - | 7 | 0.44163 | 38.02 | 52.4117 | 15.9743 | 15.2529 | 15.2529 | 8.1758 | 0.0014079 | 0.0014059 | 0.01802 | -0.0065118 | 4.0776
3559 | - | - | 7 | 0.44163 | 38.02 | 52.3903 | 15.9678 | 15.2464 | 15.2464 | 8.1772 | 0.0014059 | 0.0014039 | -0.0065118 | -0.0036079 | -3.6002
3564 | - | - | 7 | 0.44163 | 38.02 | 52.3785 | 15.9642 | 15.2428 | 15.2428 | 8.1786 | 0.0014039 | 0.0014019 | -0.0036079 | 0.0032079 | -0.13915
3569 | - | - | 7 | 0.44163 | 38.02 | 52.389 | 15.9674 | 15.246 | 15.246 | 8.18 | 0.0014019 | 0.0014 | 0.0032079 | 0.0013743 | 1.6345 | 0.011145 | 0.011022 | 0.028002 | 0.016557 | 2.0045
3574 | - | - | 7 | 0.44163 | 38.02 | 52.3935 | 15.9688 | 15.2474 | 15.2474 | 8.1814 | 0.0014 | 0.001398 | 0.0013743 | 0.00050987 | 0.67298
3579 | - | - | 7 | 0.44163 | 38.02 | 52.3952 | 15.9693 | 15.2479 | 15.2479 | 8.1828 | 0.001398 | 0.0013961 | 0.00050987 | 0.00029605 | 0.28833
3584 | - | - | 7 | 0.44163 | 38.02 | 52.3961 | 15.9696 | 15.2482 | 15.2482 | 8.1842 | 0.0013961 | 0.0013941 | 0.00029605 | 0.0087961 | 3.2629
3589 | - | - | 7 | 0.44163 | 38.02 | 52.425 | 15.9784 | 15.257 | 15.257 | 8.1856 | 0.0013941 | 0.0013922 | 0.0087961 | 0.0050158 | 4.9552
3594 | - | - | 7 | 0.44163 | 38.02 | 52.4415 | 15.9834 | 15.262 | 15.262 | 8.187 | 0.0013922 | 0.0013902 | 0.0050158 | 0 | 1.8002
3599 | - | - | 7 | 0.44163 | 38.02 | 52.4415 | 15.9834 | 15.262 | 15.262 | 8.1884 | 0.0013902 | 0.0013883 | 0 | 0.0024079 | 0.86781
3604 | - | - | 7 | 0.44163 | 38.02 | 52.4494 | 15.9858 | 15.2644 | 15.2644 | 8.1898 | 0.0013883 | 0.0013864 | 0.0024079 | 0.009602 | 4.332
3609 | - | - | 7 | 0.44163 | 38.02 | 52.4809 | 15.9954 | 15.274 | 15.274 | 8.1912 | 0.0013864 | 0.0013845 | 0.009602 | -0.0045882 | 1.8024 | 0.011022 | 0.010902 | 0.016557 | 0.0093724 | 1.1791
3614 | - | - | 7 | 0.44163 | 38.02 | 52.4658 | 15.9908 | 15.2694 | 15.2694 | 8.1926 | 0.0013845 | 0.0013826 | -0.0045882 | -1.974e-05 | -1.663
3619 | - | - | 7 | 0.44163 | 38.02 | 52.4657 | 15.9908 | 15.2694 | 15.2694 | 8.194 | 0.0013826 | 0.0013806 | -1.974e-05 | 0.0033842 | 1.2193
3624 | - | - | 7 | 0.44163 | 38.02 | 52.4768 | 15.9942 | 15.2728 | 15.2728 | 8.1953 | 0.0013806 | 0.0013787 | 0.0033842 | 0.0086079 | 4.3486
3629 | - | - | 7 | 0.44163 | 38.02 | 52.5051 | 16.0028 | 15.2814 | 15.2814 | 8.1967 | 0.0013787 | 0.0013768 | 0.0086079 | 0.0017961 | 3.7722
3634 | - | - | 7 | 0.44163 | 38.02 | 52.511 | 16.0046 | 15.2832 | 15.2832 | 8.1981 | 0.0013768 | 0.0013749 | 0.0017961 | -0.0048138 | -1.1
3639 | - | - | 7 | 0.44163 | 38.02 | 52.4952 | 15.9998 | 15.2784 | 15.2784 | 8.1995 | 0.0013749 | 0.0013731 | -0.0048138 | 0.0046842 | -0.042416
3644 | - | - | 7 | 0.44163 | 38.02 | 52.5105 | 16.0044 | 15.2831 | 15.2831 | 8.2008 | 0.0013731 | 0.0013712 | 0.0046842 | 0.0075059 | 4.4435
3649 | - | - | 7 | 0.44163 | 38.02 | 52.5352 | 16.0119 | 15.2906 | 15.2906 | 8.2022 | 0.0013712 | 0.0013693 | 0.0075059 | 0.0073862 | 5.4341 | 0.010902 | 0.010785 | 0.0093724 | 0.01253 | 1.0116
3654 | - | - | 7 | 0.44163 | 38.02 | 52.5594 | 16.0193 | 15.298 | 15.298 | 8.2036 | 0.0013693 | 0.0013674 | 0.0073862 | -0.0050803 | 0.83635
3659 | - | - | 7 | 0.44163 | 38.02 | 52.5427 | 16.0142 | 15.2929 | 15.2929 | 8.2049 | 0.0013674 | 0.0013656 | -0.0050803 | 0.0024901 | -0.94394
3664 | - | - | 7 | 0.44163 | 38.02 | 52.5509 | 16.0167 | 15.2954 | 15.2954 | 8.2063 | 0.0013656 | 0.0013637 | 0.0024901 | -0.0003079 | 0.79817
3669 | - | - | 7 | 0.44163 | 38.02 | 52.5499 | 16.0164 | 15.2951 | 15.2951 | 8.2077 | 0.0013637 | 0.0013618 | -0.0003079 | 0.0018118 | 0.55286
3674 | - | - | 7 | 0.44163 | 38.02 | 52.5558 | 16.0182 | 15.2969 | 15.2969 | 8.209 | 0.0013618 | 0.00136 | 0.0018118 | -0.003102 | -0.47645
3679 | - | - | 7 | 0.44163 | 38.02 | 52.5457 | 16.0151 | 15.2938 | 15.2938 | 8.2104 | 0.00136 | 0.0013581 | -0.003102 | -1.1844e-05 | -1.144
3684 | - | - | 7 | 0.44163 | 38.02 | 52.5456 | 16.0151 | 15.2938 | 15.2938 | 8.2118 | 0.0013581 | 0.0013563 | -1.1844e-05 | 0.0061862 | 2.2777
3689 | - | - | 7 | 0.44163 | 38.02 | 52.5659 | 16.0213 | 15.2999 | 15.2999 | 8.2131 | 0.0013563 | 0.0013545 | 0.0061862 | -0.0072921 | -0.41471 | 0.010785 | 0.01067 | 0.01253 | 0.014547 | 1.2632
3694 | - | - | 7 | 0.44163 | 38.02 | 52.542 | 16.014 | 15.2927 | 15.2927 | 8.2145 | 0.0013545 | 0.0013526 | -0.0072921 | 0.012008 | 1.7517
3699 | - | - | 7 | 0.44163 | 38.02 | 52.5814 | 16.026 | 15.3047 | 15.3047 | 8.2158 | 0.0013526 | 0.0013508 | 0.012008 | -0.0075882 | 1.6251
3704 | - | - | 7 | 0.44163 | 38.02 | 52.5565 | 16.0184 | 15.2971 | 15.2971 | 8.2172 | 0.0013508 | 0.001349 | -0.0075882 | 0.0080158 | 0.1662
3709 | - | - | 7 | 0.44163 | 38.02 | 52.5828 | 16.0265 | 15.3051 | 15.3051 | 8.2185 | 0.001349 | 0.0013472 | 0.0080158 | -0.0082118 | -0.08083
3714 | - | - | 7 | 0.44163 | 38.02 | 52.5559 | 16.0182 | 15.2969 | 15.2969 | 8.2199 | 0.0013472 | 0.0013454 | -0.0082118 | 0.0032961 | -1.82
3719 | - | - | 7 | 0.44163 | 38.02 | 52.5667 | 16.0215 | 15.3002 | 15.3002 | 8.2212 | 0.0013454 | 0.0013435 | 0.0032961 | 0.0067961 | 3.755
3724 | - | - | 7 | 0.44163 | 38.02 | 52.589 | 16.0283 | 15.307 | 15.307 | 8.2226 | 0.0013435 | 0.0013417 | 0.0067961 | 0.0055059 | 4.5806
3729 | - | - | 7 | 0.44163 | 38.02 | 52.607 | 16.0338 | 15.3125 | 15.3125 | 8.2239 | 0.0013417 | 0.0013399 | 0.0055059 | -0.0035961 | 0.70764 | 0.01067 | 0.010557 | 0.014547 | -0.0196 | -0.25512
3734 | - | - | 7 | 0.44163 | 38.02 | 52.5952 | 16.0302 | 15.3089 | 15.3089 | 8.2252 | 0.0013399 | 0.0013382 | -0.0035961 | 0.0031059 | -0.17966
3739 | - | - | 7 | 0.44163 | 38.02 | 52.6054 | 16.0334 | 15.312 | 15.312 | 8.2266 | 0.0013382 | 0.0013364 | 0.0031059 | 0.0053079 | 3.147
3744 | - | - | 7 | 0.44163 | 38.02 | 52.6228 | 16.0387 | 15.3173 | 15.3173 | 8.2279 | 0.0013364 | 0.0013346 | 0.0053079 | 0.0013079 | 2.475
3749 | - | - | 7 | 0.44163 | 38.02 | 52.6271 | 16.04 | 15.3186 | 15.3186 | 8.2292 | 0.0013346 | 0.0013328 | 0.0013079 | -0.0013882 | -0.031438
3754 | - | - | 7 | 0.44163 | 38.02 | 52.6226 | 16.0386 | 15.3172 | 15.3172 | 8.2306 | 0.0013328 | 0.001331 | -0.0013882 | 0.004998 | 1.3583
3759 | - | - | 7 | 0.44163 | 38.02 | 52.639 | 16.0436 | 15.3222 | 15.3222 | 8.2319 | 0.001331 | 0.0013293 | 0.004998 | 0.005298 | 3.8704
3764 | - | - | 7 | 0.44163 | 38.02 | 52.6564 | 16.0489 | 15.3275 | 15.3275 | 8.2332 | 0.0013293 | 0.0013275 | 0.005298 | -0.00048618 | 1.8083
3769 | - | - | 7 | 0.44163 | 38.02 | 52.6548 | 16.0484 | 15.327 | 15.327 | 8.2346 | 0.0013275 | 0.0013257 | -0.00048618 | 0.0020059 | 0.57404 | 0.010557 | 0.010447 | -0.0196 | -0.01152 | -1.4777
3774 | - | - | 7 | 0.44163 | 38.02 | 52.6613 | 16.0504 | 15.329 | 15.329 | 8.2359 | 0.0013257 | 0.001324 | 0.0020059 | -0.0023158 | -0.11911
3779 | - | - | 7 | 0.44163 | 38.02 | 52.6538 | 16.0481 | 15.3267 | 15.3267 | 8.2372 | 0.001324 | 0.0013222 | -0.0023158 | -0.014504 | -6.3623
3784 | - | - | 7 | 0.44163 | 38.02 | 52.6062 | 16.0336 | 15.3122 | 15.3122 | 8.2385 | 0.0013222 | 0.0013205 | -0.014504 | -0.006102 | -7.7931
3789 | - | - | 7 | 0.44163 | 38.02 | 52.5861 | 16.0275 | 15.3061 | 15.3061 | 8.2399 | 0.0013205 | 0.0013187 | -0.006102 | -0.0050763 | -4.2349
3794 | - | - | 7 | 0.44163 | 38.02 | 52.5695 | 16.0224 | 15.301 | 15.301 | 8.2412 | 0.0013187 | 0.001317 | -0.0050763 | 0.0045 | -0.21386
3799 | - | - | 7 | 0.44163 | 38.02 | 52.5843 | 16.0269 | 15.3055 | 15.3055 | 8.2425 | 0.001317 | 0.0013153 | 0.0045 | -0.0018941 | 0.98679
3804 | - | - | 7 | 0.44163 | 38.02 | 52.578 | 16.025 | 15.3036 | 15.3036 | 8.2438 | 0.0013153 | 0.0013135 | -0.0018941 | 0.0037862 | 0.7226
3809 | - | - | 7 | 0.44163 | 38.02 | 52.5905 | 16.0288 | 15.3074 | 15.3074 | 8.2451 | 0.0013135 | 0.0013118 | 0.0037862 | 0.002002 | 2.2038 | 0.010447 | 0.010339 | -0.01152 | -0.01708 | -1.3788
3814 | - | - | 7 | 0.44163 | 38.02 | 52.597 | 16.0308 | 15.3094 | 15.3094 | 8.2464 | 0.0013118 | 0.0013101 | 0.002002 | -0.0073079 | -2.0283
3819 | - | - | 7 | 0.44163 | 38.02 | 52.5731 | 16.0235 | 15.3021 | 15.3021 | 8.2477 | 0.0013101 | 0.0013084 | -0.0073079 | -0.0037 | -4.2021
3824 | - | - | 7 | 0.44163 | 38.02 | 52.5609 | 16.0198 | 15.2984 | 15.2984 | 8.2491 | 0.0013084 | 0.0013067 | -0.0037 | 0.007002 | 1.268
3829 | - | - | 7 | 0.44163 | 38.02 | 52.5839 | 16.0268 | 15.3054 | 15.3054 | 8.2504 | 0.0013067 | 0.001305 | 0.007002 | -0.0074039 | -0.16112
3834 | - | - | 7 | 0.44163 | 38.02 | 52.5596 | 16.0194 | 15.298 | 15.298 | 8.2517 | 0.001305 | 0.0013033 | -0.0074039 | 0.0034783 | -1.4997
3839 | - | - | 7 | 0.44163 | 38.02 | 52.571 | 16.0229 | 15.3015 | 15.3015 | 8.253 | 0.0013033 | 0.0013016 | 0.0034783 | -0.0072941 | -1.4703
3844 | - | - | 7 | 0.44163 | 38.02 | 52.5471 | 16.0156 | 15.2942 | 15.2942 | 8.2543 | 0.0013016 | 0.0012999 | -0.0072941 | 0.0017039 | -2.1443
3849 | - | - | 7 | 0.44163 | 38.02 | 52.5527 | 16.0173 | 15.2959 | 15.2959 | 8.2556 | 0.0012999 | 0.0012982 | 0.0017039 | 0.0091783 | 4.1923 | 0.010339 | 0.010233 | -0.01708 | -0.01089 | -1.3566
3854 | - | - | 7 | 0.44163 | 38.02 | 52.5828 | 16.0264 | 15.3051 | 15.3051 | 8.2569 | 0.0012982 | 0.0012965 | 0.0091783 | -0.0070763 | 0.80197
3859 | - | - | 7 | 0.44163 | 38.02 | 52.5596 | 16.0194 | 15.298 | 15.298 | 8.2582 | 0.0012965 | 0.0012948 | -0.0070763 | 0.0062 | -0.33153
3864 | - | - | 7 | 0.44163 | 38.02 | 52.5799 | 16.0256 | 15.3042 | 15.3042 | 8.2595 | 0.0012948 | 0.0012932 | 0.0062 | 0.0046 | 4.1723
3869 | - | - | 7 | 0.44163 | 38.02 | 52.595 | 16.0302 | 15.3088 | 15.3088 | 8.2608 | 0.0012932 | 0.0012915 | 0.0046 | -0.01109 | -2.5189
3874 | - | - | 7 | 0.44163 | 38.02 | 52.5586 | 16.0191 | 15.2977 | 15.2977 | 8.262 | 0.0012915 | 0.0012898 | -0.01109 | -0.0083901 | -7.5453
3879 | - | - | 7 | 0.44163 | 38.02 | 52.5311 | 16.0107 | 15.2893 | 15.2893 | 8.2633 | 0.0012898 | 0.0012882 | -0.0083901 | -0.0023059 | -4.146
3884 | - | - | 7 | 0.44163 | 38.02 | 52.5235 | 16.0084 | 15.287 | 15.287 | 8.2646 | 0.0012882 | 0.0012865 | -0.0023059 | -0.0081961 | -4.0819
3889 | - | - | 7 | 0.44163 | 38.02 | 52.4966 | 16.0002 | 15.2788 | 15.2788 | 8.2659 | 0.0012865 | 0.0012849 | -0.0081961 | -0.0083961 | -6.4528 | 0.010233 | 0.010129 | -0.01089 | 0.013663 | 0.14847
3894 | - | - | 7 | 0.44163 | 38.02 | 52.4691 | 15.9918 | 15.2704 | 15.2704 | 8.2672 | 0.0012849 | 0.0012832 | -0.0083961 | -0.00048816 | -3.4556
3899 | - | - | 7 | 0.44163 | 38.02 | 52.4675 | 15.9913 | 15.2699 | 15.2699 | 8.2685 | 0.0012832 | 0.0012816 | -0.00048816 | -0.0032 | -1.4394
3904 | - | - | 7 | 0.44163 | 38.02 | 52.457 | 15.9881 | 15.2667 | 15.2667 | 8.2698 | 0.0012816 | 0.0012799 | -0.0032 | 0.005702 | 0.98122
3909 | - | - | 7 | 0.44163 | 38.02 | 52.4757 | 15.9938 | 15.2724 | 15.2724 | 8.271 | 0.0012799 | 0.0012783 | 0.005702 | 0.0032 | 3.4785
3914 | - | - | 7 | 0.44163 | 38.02 | 52.4862 | 15.997 | 15.2756 | 15.2756 | 8.2723 | 0.0012783 | 0.0012767 | 0.0032 | -0.004602 | -0.55263
3919 | - | - | 7 | 0.44163 | 38.02 | 52.4711 | 15.9924 | 15.271 | 15.271 | 8.2736 | 0.0012767 | 0.001275 | -0.004602 | -0.008002 | -4.9412
3924 | - | - | 7 | 0.44163 | 38.02 | 52.4448 | 15.9844 | 15.263 | 15.263 | 8.2749 | 0.001275 | 0.0012734 | -0.008002 | 0.0048961 | -1.2123
3929 | - | - | 7 | 0.44163 | 38.02 | 52.4609 | 15.9893 | 15.2679 | 15.2679 | 8.2761 | 0.0012734 | 0.0012718 | 0.0048961 | 0.001898 | 2.6679 | 0.010129 | 0.010028 | 0.013663 | 0.020428 | 1.6947
3934 | - | - | 7 | 0.44163 | 38.02 | 52.4671 | 15.9912 | 15.2698 | 15.2698 | 8.2774 | 0.0012718 | 0.0012702 | 0.001898 | 0.0022197 | 1.6201
3939 | - | - | 7 | 0.44163 | 38.02 | 52.4744 | 15.9934 | 15.272 | 15.272 | 8.2787 | 0.0012702 | 0.0012686 | 0.0022197 | 0.0070039 | 3.6356
3944 | - | - | 7 | 0.44163 | 38.02 | 52.4974 | 16.0004 | 15.2791 | 15.2791 | 8.28 | 0.0012686 | 0.0012669 | 0.0070039 | -0.004298 | 1.0616
3949 | - | - | 7 | 0.44163 | 38.02 | 52.4833 | 15.9961 | 15.2748 | 15.2748 | 8.2812 | 0.0012669 | 0.0012653 | -0.004298 | -0.0028 | -2.8023
3954 | - | - | 7 | 0.44163 | 38.02 | 52.4741 | 15.9933 | 15.272 | 15.272 | 8.2825 | 0.0012653 | 0.0012637 | -0.0028 | 0.011122 | 3.2974
3959 | - | - | 7 | 0.44163 | 38.02 | 52.5106 | 16.0044 | 15.2831 | 15.2831 | 8.2837 | 0.0012637 | 0.0012621 | 0.011122 | -0.00029408 | 4.281
3964 | - | - | 7 | 0.44163 | 38.02 | 52.5096 | 16.0042 | 15.2828 | 15.2828 | 8.285 | 0.0012621 | 0.0012606 | -0.00029408 | -0.0011882 | -0.588
3969 | - | - | 7 | 0.44163 | 38.02 | 52.5057 | 16.003 | 15.2816 | 15.2816 | 8.2863 | 0.0012606 | 0.001259 | -0.0011882 | 0.0042079 | 1.2012 | 0.010028 | 0.0099281 | 0.020428 | 0.027426 | 2.4016
3974 | - | - | 7 | 0.44163 | 38.02 | 52.5195 | 16.0072 | 15.2858 | 15.2858 | 8.2875 | 0.001259 | 0.0012574 | 0.0042079 | 0.0122 | 6.5245
3979 | - | - | 7 | 0.44163 | 38.02 | 52.5596 | 16.0194 | 15.298 | 15.298 | 8.2888 | 0.0012574 | 0.0012558 | 0.0122 | -0.0072882 | 1.9447
3984 | - | - | 7 | 0.44163 | 38.02 | 52.5356 | 16.0121 | 15.2907 | 15.2907 | 8.29 | 0.0012558 | 0.0012542 | -0.0072882 | -0.001602 | -3.539
3989 | - | - | 7 | 0.44163 | 38.02 | 52.5304 | 16.0105 | 15.2891 | 15.2891 | 8.2913 | 0.0012542 | 0.0012527 | -0.001602 | 0.00011777 | -0.59119
3994 | - | - | 7 | 0.44163 | 38.02 | 52.5308 | 16.0106 | 15.2892 | 15.2892 | 8.2925 | 0.0012527 | 0.0012511 | 0.00011777 | 0.00069803 | 0.32612
3999 | - | - | 7 | 0.44163 | 38.02 | 52.5331 | 16.0113 | 15.2899 | 15.2899 | 8.2938 | 0.0012511 | 0.0012495 | 0.00069803 | 0.010098 | 4.322
4004 | - | - | 7 | 0.44163 | 38.02 | 52.5662 | 16.0214 | 15.3 | 15.3 | 8.295 | 0.0012495 | 0.001248 | 0.010098 | 0.0019961 | 4.8384
4009 | - | - | 7 | 0.44163 | 38.02 | 52.5727 | 16.0234 | 15.302 | 15.302 | 8.2963 | 0.001248 | 0.0012464 | 0.0019961 | -0.0026901 | -0.2806 | 0.0099281 | 0.0098305 | 0.027426 | 0.021038 | 2.4497
4014 | - | - | 7 | 0.44163 | 38.02 | 52.5639 | 16.0207 | 15.2993 | 15.2993 | 8.2975 | 0.0012464 | 0.0012449 | -0.0026901 | -0.0051 | -3.1282
4019 | - | - | 7 | 0.44163 | 38.02 | 52.5472 | 16.0156 | 15.2942 | 15.2942 | 8.2988 | 0.0012449 | 0.0012433 | -0.0051 | 0.0058039 | 0.28837
4024 | - | - | 7 | 0.44163 | 38.02 | 52.5662 | 16.0214 | 15.3 | 15.3 | 8.3 | 0.0012433 | 0.0012418 | 0.0058039 | 0.009398 | 6.1191
4029 | - | - | 7 | 0.44163 | 38.02 | 52.5971 | 16.0308 | 15.3094 | 15.3094 | 8.3013 | 0.0012418 | 0.0012402 | 0.009398 | -0.0041941 | 2.0899
4034 | - | - | 7 | 0.44163 | 38.02 | 52.5833 | 16.0266 | 15.3052 | 15.3052 | 8.3025 | 0.0012402 | 0.0012387 | -0.0041941 | 0.010994 | 2.7507
4039 | - | - | 7 | 0.44163 | 38.02 | 52.6194 | 16.0376 | 15.3162 | 15.3162 | 8.3038 | 0.0012387 | 0.0012372 | 0.010994 | 0.0083237 | 7.8011
4044 | - | - | 7 | 0.44163 | 38.02 | 52.6467 | 16.0459 | 15.3246 | 15.3246 | 8.305 | 0.0012372 | 0.0012356 | 0.0083237 | 0.0048901 | 5.342
4049 | - | - | 7 | 0.44163 | 38.02 | 52.6627 | 16.0508 | 15.3294 | 15.3294 | 8.3062 | 0.0012356 | 0.0012341 | 0.0048901 | 0.00058026 | 2.2128 | 0.0098305 | 0.0097348 | 0.021038 | 0.018553 | 2.0224
4054 | - | - | 7 | 0.44163 | 38.02 | 52.6646 | 16.0514 | 15.33 | 15.33 | 8.3075 | 0.0012341 | 0.0012326 | 0.00058026 | 0.012398 | 5.2673
4059 | - | - | 7 | 0.44163 | 38.02 | 52.7053 | 16.0638 | 15.3424 | 15.3424 | 8.3087 | 0.0012326 | 0.0012311 | 0.012398 | -0.0011 | 4.5791
4064 | - | - | 7 | 0.44163 | 38.02 | 52.7017 | 16.0627 | 15.3413 | 15.3413 | 8.3099 | 0.0012311 | 0.0012296 | -0.0011 | 0.0072257 | 2.4936
4069 | - | - | 7 | 0.44163 | 38.02 | 52.7254 | 16.0699 | 15.3486 | 15.3486 | 8.3112 | 0.0012296 | 0.001228 | 0.0072257 | -0.0032783 | 1.6009
4074 | - | - | 7 | 0.44163 | 38.02 | 52.7147 | 16.0666 | 15.3453 | 15.3453 | 8.3124 | 0.001228 | 0.0012265 | -0.0032783 | 0.00038816 | -1.1756
4079 | - | - | 7 | 0.44163 | 38.02 | 52.7159 | 16.067 | 15.3457 | 15.3457 | 8.3136 | 0.0012265 | 0.001225 | 0.00038816 | 0.0019079 | 0.93732
4084 | - | - | 7 | 0.44163 | 38.02 | 52.7222 | 16.0689 | 15.3476 | 15.3476 | 8.3148 | 0.001225 | 0.0012235 | 0.0019079 | 0.0029158 | 1.9705
4089 | - | - | 7 | 0.44163 | 38.02 | 52.7318 | 16.0719 | 15.3505 | 15.3505 | 8.3161 | 0.0012235 | 0.001222 | 0.0029158 | 0.00099408 | 1.5978 | 0.0097348 | 0.009641 | 0.018553 | -0.0018507 | 0.85188
4094 | - | - | 7 | 0.44163 | 38.02 | 52.735 | 16.0728 | 15.3515 | 15.3515 | 8.3173 | 0.001222 | 0.0012206 | 0.00099408 | 0.0034039 | 1.8018
4099 | - | - | 7 | 0.44163 | 38.02 | 52.7462 | 16.0763 | 15.3549 | 15.3549 | 8.3185 | 0.0012206 | 0.0012191 | 0.0034039 | 0.001002 | 1.8048
4104 | - | - | 7 | 0.44163 | 38.02 | 52.7495 | 16.0773 | 15.3559 | 15.3559 | 8.3197 | 0.0012191 | 0.0012176 | 0.001002 | 0.011812 | 5.2642
4109 | - | - | 7 | 0.44163 | 38.02 | 52.7882 | 16.0891 | 15.3677 | 15.3677 | 8.3209 | 0.0012176 | 0.0012161 | 0.011812 | -0.0063921 | 2.2179
4114 | - | - | 7 | 0.44163 | 38.02 | 52.7673 | 16.0827 | 15.3613 | 15.3613 | 8.3222 | 0.0012161 | 0.0012146 | -0.0063921 | 0.0060178 | -0.1478
4119 | - | - | 7 | 0.44163 | 38.02 | 52.787 | 16.0887 | 15.3673 | 15.3673 | 8.3234 | 0.0012146 | 0.0012132 | 0.0060178 | -0.0061822 | -0.073844
4124 | - | - | 7 | 0.44163 | 38.02 | 52.7667 | 16.0825 | 15.3611 | 15.3611 | 8.3246 | 0.0012132 | 0.0012117 | -0.0061822 | 0.007898 | 0.71463
4129 | - | - | 7 | 0.44163 | 38.02 | 52.7926 | 16.0904 | 15.369 | 15.369 | 8.3258 | 0.0012117 | 0.0012102 | 0.007898 | 0.008298 | 6.6876 | 0.009641 | 0.0095489 | -0.0018507 | 0.015663 | 0.72857
4134 | - | - | 7 | 0.44163 | 38.02 | 52.8199 | 16.0987 | 15.3773 | 15.3773 | 8.327 | 0.0012102 | 0.0012088 | 0.008298 | -0.0074118 | 0.35849
4139 | - | - | 7 | 0.44163 | 38.02 | 52.7955 | 16.0913 | 15.3699 | 15.3699 | 8.3282 | 0.0012088 | 0.0012073 | -0.0074118 | 0.0039178 | -1.4405
4144 | - | - | 7 | 0.44163 | 38.02 | 52.8084 | 16.0952 | 15.3738 | 15.3738 | 8.3294 | 0.0012073 | 0.0012058 | 0.0039178 | -0.0048783 | -0.40244
4149 | - | - | 7 | 0.44163 | 38.02 | 52.7924 | 16.0903 | 15.369 | 15.369 | 8.3306 | 0.0012058 | 0.0012044 | -0.0048783 | 0.005602 | 0.3055
4154 | - | - | 7 | 0.44163 | 38.02 | 52.8108 | 16.0959 | 15.3746 | 15.3746 | 8.3318 | 0.0012044 | 0.0012029 | 0.005602 | -0.0048862 | 0.2921
4159 | - | - | 7 | 0.44163 | 38.02 | 52.7947 | 16.091 | 15.3697 | 15.3697 | 8.333 | 0.0012029 | 0.0012015 | -0.0048862 | 0.0087059 | 1.5954
4164 | - | - | 7 | 0.44163 | 38.02 | 52.8233 | 16.0998 | 15.3784 | 15.3784 | 8.3342 | 0.0012015 | 0.0012 | 0.0087059 | -0.011198 | -1.0477
4169 | - | - | 7 | 0.44163 | 38.02 | 52.7866 | 16.0886 | 15.3672 | 15.3672 | 8.3354 | 0.0012 | 0.0011986 | -0.011198 | 0.0064961 | -1.9514 | 0.0095489 | 0.0094586 | 0.015663 | 0.013501 | 1.5333
4174 | - | - | 7 | 0.44163 | 38.02 | 52.8079 | 16.0951 | 15.3737 | 15.3737 | 8.3366 | 0.0011986 | 0.0011972 | 0.0064961 | -0.0080612 | -0.66057
4179 | - | - | 7 | 0.44163 | 38.02 | 52.7814 | 16.087 | 15.3656 | 15.3656 | 8.3378 | 0.0011972 | 0.0011957 | -0.0080612 | -0.0010395 | -3.7997
4184 | - | - | 7 | 0.44163 | 38.02 | 52.778 | 16.086 | 15.3646 | 15.3646 | 8.339 | 0.0011957 | 0.0011943 | -0.0010395 | 0.0026276 | 0.66632
4189 | - | - | 7 | 0.44163 | 38.02 | 52.7866 | 16.0886 | 15.3672 | 15.3672 | 8.3402 | 0.0011943 | 0.0011929 | 0.0026276 | 0.0077395 | 4.3453
4194 | - | - | 7 | 0.44163 | 38.02 | 52.812 | 16.0963 | 15.3749 | 15.3749 | 8.3414 | 0.0011929 | 0.0011915 | 0.0077395 | 0.0010434 | 3.6802
4199 | - | - | 7 | 0.44163 | 38.02 | 52.8154 | 16.0974 | 15.376 | 15.376 | 8.3426 | 0.0011915 | 0.0011901 | 0.0010434 | 0.0061316 | 3.0153
4204 | - | - | 7 | 0.44163 | 38.02 | 52.8356 | 16.1035 | 15.3821 | 15.3821 | 8.3438 | 0.0011901 | 0.0011886 | 0.0061316 | 0.00072566 | 2.8801
4209 | - | - | 7 | 0.44163 | 38.02 | 52.8379 | 16.1042 | 15.3828 | 15.3828 | 8.345 | 0.0011886 | 0.0011872 | 0.00072566 | 0.0039375 | 1.9643 | 0.0094586 | 0.0093699 | 0.013501 | 0.037932 | 2.744
4214 | - | - | 7 | 0.44163 | 38.02 | 52.8509 | 16.1082 | 15.3868 | 15.3868 | 8.3462 | 0.0011872 | 0.0011858 | 0.0039375 | -0.00057236 | 1.4158
4219 | - | - | 7 | 0.44163 | 38.02 | 52.849 | 16.1076 | 15.3862 | 15.3862 | 8.3474 | 0.0011858 | 0.0011844 | -0.00057236 | 0.0020197 | 0.61194
4224 | - | - | 7 | 0.44163 | 38.02 | 52.8556 | 16.1096 | 15.3882 | 15.3882 | 8.3485 | 0.0011844 | 0.001183 | 0.0020197 | 0.0041237 | 2.596
4229 | - | - | 7 | 0.44163 | 38.02 | 52.8691 | 16.1137 | 15.3924 | 15.3924 | 8.3497 | 0.001183 | 0.0011816 | 0.0041237 | 0.0093316 | 5.6928
4234 | - | - | 7 | 0.44163 | 38.02 | 52.8998 | 16.1231 | 15.4017 | 15.4017 | 8.3509 | 0.0011816 | 0.0011802 | 0.0093316 | -0.0038316 | 2.3221
4239 | - | - | 7 | 0.44163 | 38.02 | 52.8872 | 16.1192 | 15.3979 | 15.3979 | 8.3521 | 0.0011802 | 0.0011788 | -0.0038316 | 0.0103 | 2.749
4244 | - | - | 7 | 0.44163 | 38.02 | 52.921 | 16.1295 | 15.4082 | 15.4082 | 8.3533 | 0.0011788 | 0.0011774 | 0.0103 | -0.011808 | -0.65101
4249 | - | - | 7 | 0.44163 | 38.02 | 52.8822 | 16.1177 | 15.3964 | 15.3964 | 8.3544 | 0.0011774 | 0.0011761 | -0.011808 | 0.010994 | -0.33439 | 0.0093699 | -2.1879 | 0.037932 | -5.6095 | 4.0546
4254 | - | - | 7 | 0.44163 | 38.02 | 52.9183 | 16.1287 | 15.4073 | 15.4073 | 8.3556 | 0.0011761 | 0.0011747 | 0.010994 | -0.0015763 | 4
4259 | - | - | 7 | 0.44163 | 38.02 | 52.9131 | 16.1271 | 15.4058 | 15.4058 | 8.3568 | 0.0011747 | 0.0011733 | -0.0015763 | -0.00091184 | -1.0594
4264 | - | - | 7 | 0.44163 | 38.02 | 52.9101 | 16.1262 | 15.4049 | 15.4049 | 8.358 | 0.0011733 | 0.0011719 | -0.00091184 | 0.0070276 | 2.6117
4269 | - | - | 7 | 0.44163 | 38.02 | 52.9332 | 16.1333 | 15.4119 | 15.4119 | 8.3591 | 0.0011719 | 0.0011705 | 0.0070276 | 0.0012704 | 3.5395
4274 | - | - | 7 | 0.44163 | 38.02 | 52.9374 | 16.1345 | 15.4132 | 15.4132 | 8.3603 | 0.0011705 | 0.0011692 | 0.0012704 | -0.00086644 | 0.17158
4279 | - | - | 7 | 0.44163 | 38.02 | 52.9345 | 16.1337 | 15.4123 | 15.4123 | 8.3615 | 0.0011692 | 0.0011678 | -0.00086644 | 0.01659 | 6.7369
4284 | - | - | 7 | 0.44163 | 38.02 | 52.989 | 16.1502 | 15.4289 | 15.4289 | 8.3626 | 0.0011678 | 0.0011665 | 0.01659 | 0.0054039 | 9.4167
4289 | - | - | 7 | 0.44163 | 38.02 | 53.0067 | 16.1557 | 15.4343 | 15.4343 | 8.3638 | 0.0011665 | 0.0011651 | 0.0054039 | -0.00047631 | 2.1105 | -2.1879 | -1.6854 | -5.6095 | -3.4183 | 2.2613
4294 | - | - | 7 | 0.44163 | 38.02 | 53.0051 | 16.1552 | 15.4338 | 15.4338 | 8.365 | 0.0011651 | 0.0011637 | -0.00047631 | 0.0087197 | 3.5443
4299 | - | - | 7 | 0.44163 | 38.02 | 53.0337 | 16.1639 | 15.4425 | 15.4425 | 8.3661 | 0.0011637 | 0.0011624 | 0.0087197 | -0.0053059 | 1.4606
4304 | - | - | 7 | 0.44163 | 38.02 | 53.0163 | 16.1586 | 15.4372 | 15.4372 | 8.3673 | 0.0011624 | 0.001161 | -0.0053059 | 0.0064585 | 0.50197
4309 | - | - | 7 | 0.44163 | 38.02 | 53.0375 | 16.165 | 15.4437 | 15.4437 | 8.3685 | 0.001161 | 0.0011597 | 0.0064585 | -0.0043079 | 0.92133
4314 | - | - | 7 | 0.44163 | 38.02 | 53.0234 | 16.1607 | 15.4394 | 15.4394 | 8.3696 | 0.0011597 | 0.0011583 | -0.0043079 | 0.0011921 | -1.3414
4319 | - | - | 7 | 0.44163 | 38.02 | 53.0273 | 16.1619 | 15.4406 | 15.4406 | 8.3708 | 0.0011583 | #VALUE! | 0.0011921 | -3.8284 | #VALUE!
4324 | 4 | 1081 | 0 | 0 | 0 | 40.4664 | 12.3336 | 11.6122 | 14.5871 | ln(t/t') | D(t/t')1 | D(t/t')2 | Ds1 | Ds2 | ds/d(t/t') | D(t/t')1 | D(t/t')2 | Ds1 | Ds2 | ds/d(t/t') (L-Spacing = 8) | d2s/d(t/t')2
4329 | 9 | 481 | 0 | 0 | 0 | 34.6019 | 10.5462 | 9.8248 | 14.3422 | 6.1759 | #VALUE! | -0.44068 | -1.7874 | -1.0218 | #VALUE! | -1.6854 | -0.5877 | -3.4183 | -0.88844 | 1.6453
4334 | 14 | 309.5714 | 0 | 0 | 0 | 31.2493 | 9.5243 | 8.803 | 14.2903 | 5.7352 | -0.44068 | -0.30423 | -1.0218 | -0.66417 | 2.2385
4339 | 19 | 228.3684 | 0 | 0 | 0 | 29.0702 | 8.8602 | 8.1388 | 14.2868 | 5.431 | -0.30423 | -0.23246 | -0.66417 | -0.46911 | 2.0895
4344 | 24 | 181 | 0 | 0 | 0 | 27.5311 | 8.3911 | 7.6697 | 14.304 | 5.1985 | -0.23246 | -0.18809 | -0.46911 | -0.3599 | 1.9602
4349 | 29 | 149.9655 | 0 | 0 | 0 | 26.3502 | 8.0312 | 7.3098 | 14.3452 | 5.0104 | -0.18809 | -0.15792 | -0.3599 | -0.28801 | 1.8647
4354 | 34 | 128.0588 | 0 | 0 | 0 | 25.4053 | 7.7431 | 7.0218 | 14.3778 | 4.8525 | -0.15792 | -0.13605 | -0.28801 | -0.23736 | 1.7813
4359 | 39 | 111.7692 | 0 | 0 | 0 | 24.6265 | 7.5058 | 6.7844 | 14.413 | 4.7164 | -0.13605 | -0.11948 | -0.23736 | -0.20049 | 1.7092
4364 | 44 | 99.1818 | 0 | 0 | 0 | 23.9687 | 7.3053 | 6.5839 | 14.4485 | 4.597 | -0.11948 | -0.10649 | -0.20049 | -0.17742 | 1.6717
4369 | 49 | 89.1633 | 0 | 0 | 0 | 23.3865 | 7.1279 | 6.4065 | 14.4922 | 4.4905 | -0.10649 | -0.09602 | -0.17742 | -0.15552 | 1.6417 | -0.5877 | -0.36214 | -0.88844 | -0.49776 | 1.4268
4374 | 54 | 81 | 0 | 0 | 0 | 22.8763 | 6.9724 | 6.251 | 14.5256 | 4.3944 | -0.09602 | -0.087411 | -0.15552 | -0.13654 | 1.5895
4379 | 59 | 74.2203 | 0 | 0 | 0 | 22.4283 | 6.8358 | 6.1144 | 14.5628 | 4.307 | -0.087411 | -0.080204 | -0.13654 | -0.12805 | 1.58
4384 | 64 | 68.5 | 0 | 0 | 0 | 22.0082 | 6.7078 | 5.9864 | 14.5197 | 4.2268 | -0.080204 | -0.074084 | -0.12805 | -0.10865 | 1.529
4389 | 69 | 63.6087 | 0 | 0 | 0 | 21.6517 | 6.5991 | 5.8777 | 14.4889 | 4.1528 | -0.074084 | -0.06882 | -0.10865 | -0.09898 | 1.4519
4394 | 74 | 59.3784 | 0 | 0 | 0 | 21.3269 | 6.5001 | 5.7788 | 14.4852 | 4.0839 | -0.06882 | -0.064245 | -0.09898 | -0.090166 | 1.4203
4399 | 79 | 55.6835 | 0 | 0 | 0 | 21.0311 | 6.41 | 5.6886 | 14.4854 | 4.0197 | -0.064245 | -0.060233 | -0.090166 | -0.088545 | 1.4378
4404 | 84 | 52.4286 | 0 | 0 | 0 | 20.7406 | 6.3214 | 5.6001 | 14.5084 | 3.9595 | -0.060233 | -0.056685 | -0.088545 | -0.081998 | 1.4579
4409 | 89 | 49.5393 | 0 | 0 | 0 | 20.4716 | 6.2394 | 5.5181 | 14.5318 | 3.9028 | -0.056685 | -0.053525 | -0.081998 | -0.074388 | 1.4174 | -0.36214 | -0.26114 | -0.49776 | -0.35013 | 1.3549
4414 | 94 | 46.9574 | 0 | 0 | 0 | 20.2275 | 6.165 | 5.4437 | 14.5464 | 3.8492 | -0.053525 | -0.050693 | -0.074388 | -0.071322 | 1.3986
4419 | 99 | 44.6364 | 0 | 0 | 0 | 19.9935 | 6.0937 | 5.3723 | 14.5589 | 3.7985 | -0.050693 | -0.04814 | -0.071322 | -0.06621 | 1.3907
4424 | 104 | 42.5385 | 0 | 0 | 0 | 19.7762 | 6.0275 | 5.3061 | 14.5753 | 3.7504 | -0.04814 | -0.045827 | -0.06621 | -0.06269 | 1.3716
4429 | 109 | 40.633 | 0 | 0 | 0 | 19.5706 | 5.9648 | 5.2434 | 14.5799 | 3.7046 | -0.045827 | -0.043722 | -0.06269 | -0.060318 | 1.3739
4434 | 114 | 38.8947 | 0 | 0 | 0 | 19.3727 | 5.9045 | 5.1831 | 14.5859 | 3.6609 | -0.043722 | -0.041798 | -0.060318 | -0.056724 | 1.3681
4439 | 119 | 37.3025 | 0 | 0 | 0 | 19.1865 | 5.8478 | 5.1264 | 14.5939 | 3.6191 | -0.041798 | -0.040032 | -0.056724 | -0.055106 | 1.367
4444 | 124 | 35.8387 | 0 | 0 | 0 | 19.0057 | 5.7927 | 5.0713 | 14.6071 | 3.579 | -0.040032 | -0.038406 | -0.055106 | -0.051002 | 1.3517
4449 | 129 | 34.4884 | 0 | 0 | 0 | 18.8384 | 5.7417 | 5.0203 | 14.6185 | 3.5406 | -0.038406 | -0.036904 | -0.051002 | -0.047476 | 1.3068 | -0.26114 | -0.20356 | -0.35013 | -0.28182 | 1.3653
4454 | 134 | 33.2388 | 0 | 0 | 0 | 18.6826 | 5.6942 | 4.9728 | 14.6319 | 3.5037 | -0.036904 | -0.035512 | -0.047476 | -0.046736 | 1.3015
4459 | 139 | 32.0791 | 0 | 0 | 0 | 18.5293 | 5.6475 | 4.9261 | 14.6407 | 3.4682 | -0.035512 | -0.034219 | -0.046736 | -0.047098 | 1.3468
4464 | 144 | 31 | 0 | 0 | 0 | 18.3748 | 5.6004 | 4.879 | 14.6533 | 3.434 | -0.034219 | -0.033014 | -0.047098 | -0.045688 | 1.3802
4469 | 149 | 29.9933 | 0 | 0 | 0 | 18.2249 | 5.5547 | 4.8333 | 14.6681 | 3.401 | -0.033014 | -0.031888 | -0.045688 | -0.042288 | 1.3545
4474 | 154 | 29.0519 | 0 | 0 | 0 | 18.0861 | 5.5124 | 4.791 | 14.6816 | 3.3691 | -0.031888 | -0.030835 | -0.042288 | -0.041204 | 1.3313
4479 | 159 | 28.1698 | 0 | 0 | 0 | 17.9509 | 5.4712 | 4.7498 | 14.6832 | 3.3383 | -0.030835 | -0.029847 | -0.041204 | -0.043424 | 1.3966
4484 | 164 | 27.3415 | 0 | 0 | 0 | 17.8085 | 5.4278 | 4.7064 | 14.7004 | 3.3084 | -0.029847 | -0.028918 | -0.043424 | -0.036212 | 1.352
4489 | 169 | 26.5621 | 0 | 0 | 0 | 17.6896 | 5.3915 | 4.6702 | 14.7197 | 3.2795 | -0.028918 | -0.028043 | -0.036212 | -0.040896 | 1.3569 | -0.20356 | -0.16633 | -0.28182 | -0.23922 | 1.4141
4494 | 174 | 25.8276 | 0 | 0 | 0 | 17.5555 | 5.3506 | 4.6293 | 14.7279 | 3.2514 | -0.028043 | -0.027219 | -0.040896 | -0.034794 | 1.367
4499 | 179 | 25.1341 | 0 | 0 | 0 | 17.4413 | 5.3159 | 4.5945 | 14.7412 | 3.2242 | -0.027219 | -0.026439 | -0.034794 | -0.038994 | 1.378
4504 | 184 | 24.4783 | 0 | 0 | 0 | 17.3134 | 5.2769 | 4.5555 | 14.7434 | 3.1978 | -0.026439 | -0.025702 | -0.038994 | -0.035104 | 1.4196
4509 | 189 | 23.8571 | 0 | 0 | 0 | 17.1982 | 5.2418 | 4.5204 | 14.7531 | 3.1721 | -0.025702 | -0.025003 | -0.035104 | -0.032122 | 1.3247
4514 | 194 | 23.268 | 0 | 0 | 0 | 17.0928 | 5.2096 | 4.4883 | 14.7731 | 3.1471 | -0.025003 | -0.02434 | -0.032122 | -0.03581 | 1.3792
4519 | 199 | 22.7085 | 0 | 0 | 0 | 16.9753 | 5.1738 | 4.4525 | 14.7722 | 3.1227 | -0.02434 | -0.023709 | -0.03581 | -0.035492 | 1.4843
4524 | 204 | 22.1765 | 0 | 0 | 0 | 16.8589 | 5.1383 | 4.417 | 14.7829 | 3.099 | -0.023709 | -0.02311 | -0.035492 | -0.028604 | 1.3657
4529 | 209 | 21.6699 | 0 | 0 | 0 | 16.765 | 5.1097 | 4.3884 | 14.7876 | 3.0759 | -0.02311 | -0.022538 | -0.028604 | -0.033514 | 1.3639 | -0.16633 | -0.14026 | -0.23922 | -0.20855 | 1.4647
4534 | 214 | 21.1869 | 0 | 0 | 0 | 16.655 | 5.0762 | 4.3548 | 14.7974 | 3.0534 | -0.022538 | -0.021994 | -0.033514 | -0.030196 | 1.4293
4539 | 219 | 20.726 | 0 | 0 | 0 | 16.556 | 5.046 | 4.3246 | 14.8075 | 3.0314 | -0.021994 | -0.021473 | -0.030196 | -0.0315 | 1.4205
4544 | 224 | 20.2857 | 0 | 0 | 0 | 16.4526 | 5.0145 | 4.2931 | 14.814 | 3.0099 | -0.021473 | -0.020976 | -0.0315 | -0.032016 | 1.497
4549 | 229 | 19.8646 | 0 | 0 | 0 | 16.3476 | 4.9825 | 4.2611 | 14.8162 | 2.9889 | -0.020976 | -0.020501 | -0.032016 | -0.026686 | 1.4127
4554 | 234 | 19.4615 | 0 | 0 | 0 | 16.26 | 4.9558 | 4.2344 | 14.8252 | 2.9684 | -0.020501 | -0.020045 | -0.026686 | -0.028212 | 1.3552
4559 | 239 | 19.0753 | 0 | 0 | 0 | 16.1675 | 4.9276 | 4.2062 | 14.8298 | 2.9484 | -0.020045 | -0.019609 | -0.028212 | -0.029264 | 1.4504
4564 | 244 | 18.7049 | 0 | 0 | 0 | 16.0714 | 4.8983 | 4.177 | 14.8356 | 2.9288 | -0.019609 | -0.01919 | -0.029264 | -0.027836 | 1.4713
4569 | 249 | 18.3494 | 0 | 0 | 0 | 15.9801 | 4.8705 | 4.1491 | 14.8387 | 2.9096 | -0.01919 | -0.018788 | -0.027836 | -0.028998 | 1.4975 | -0.14026 | -0.12099 | -0.20855 | 0.024276 | 0.5809
4574 | 254 | 18.0079 | 0 | 0 | 0 | 15.885 | 4.8415 | 4.1201 | 14.8371 | 2.8908 | -0.018788 | -0.018401 | -0.028998 | -0.0273 | 1.5132
4579 | 259 | 17.6795 | 0 | 0 | 0 | 15.7954 | 4.8142 | 4.0928 | 14.8366 | 2.8724 | -0.018401 | -0.01803 | -0.0273 | -0.023396 | 1.3897
4584 | 264 | 17.3636 | 0 | 0 | 0 | 15.7186 | 4.7908 | 4.0694 | 14.8522 | 2.8544 | -0.01803 | -0.017672 | -0.023396 | -0.030694 | 1.5195
4589 | 269 | 17.0595 | 0 | 0 | 0 | 15.6179 | 4.7601 | 4.0387 | 14.8502 | 2.8367 | -0.017672 | -0.017328 | -0.030694 | -0.025114 | 1.5917
4594 | 274 | 16.7664 | 0 | 0 | 0 | 15.5355 | 4.735 | 4.0136 | 14.8545 | 2.8194 | -0.017328 | -0.016996 | -0.025114 | -0.024608 | 1.4486
4599 | 279 | 16.4839 | 0 | 0 | 0 | 15.4548 | 4.7104 | 3.989 | 14.8594 | 2.8024 | -0.016996 | -0.016676 | -0.024608 | -0.022516 | 1.3986
4604 | 284 | 16.2113 | 0 | 0 | 0 | 15.3809 | 4.6879 | 3.9665 | 14.8594 | 2.7857 | -0.016676 | -0.016367 | -0.022516 | -0.025924 | 1.4681
4609 | 289 | 15.9481 | 0 | 0 | 0 | 15.2959 | 4.662 | 3.9406 | 14.8522 | 2.7693 | -0.016367 | -0.016069 | -0.025924 | -0.024696 | 1.5602 | -0.12099 | -0.10617 | 0.024276 | -0.29209 | 1.3715
4614 | 294 | 15.6939 | 0 | 0 | 0 | 15.2148 | 4.6373 | 3.9159 | 14.8646 | 2.7533 | -0.016069 | -0.015781 | -0.024696 | -0.0239 | 1.5256
4619 | 299 | 15.4482 | 0 | 0 | 0 | 15.1364 | 4.6134 | 3.892 | 14.8611 | 2.7375 | -0.015781 | -0.015502 | -0.0239 | -3.892 | 127.398
4624 | 304 | 15.2105 | 0 | 0 | 0 | 0 |  |  | 10.9976 | 2.722 | -0.015502 | -0.015233 | -3.892 | 0 | 124.4297
4629 | 309 | 14.9806 | 0 | 0 | 0 | 0 |  |  | 11.0205 | 2.7068 | -0.015233 | -0.014972 | 0 | 0 | 0
4634 | 314 | 14.758 | 0 | 0 | 0 | 0 |  |  | 11.0473 | 2.6918 | -0.014972 | -0.01472 | 0 | 4.1574 | -142.4178
4639 | 319 | 14.5423 | 0 | 0 | 0 | 16.0071 | 4.8787 | 4.1574 | 15.2338 | 2.6771 | -0.01472 | -0.014475 | 4.1574 | -0.11809 | -135.9211
4644 | 324 | 14.3333 | 0 | 0 | 0 | 15.6196 | 4.7606 | 4.0393 | 15.1419 | 2.6626 | -0.014475 | -0.014238 | -0.11809 | -0.074406 | 6.6799
4649 | 329 | 14.1307 | 0 | 0 | 0 | 15.3755 | 4.6862 | 3.9649 | 15.0827 | 2.6483 | -0.014238 | -0.014008 | -0.074406 | -0.055432 | 4.5863 | -0.10617 | -0.094424 | -0.29209 | -0.17491 | 2.2755
4654 | 334 | 13.9341 | 0 | 0 | 0 | 15.1936 | 4.6308 | 3.9094 | 15.0543 | 2.6343 | -0.014008 | -0.013785 | -0.055432 | -0.04939 | 3.7684
4659 | 339 | 13.7434 | 0 | 0 | 0 | 15.0316 | 4.5814 | 3.86 | 15.0304 | 2.6206 | -0.013785 | -0.013569 | -0.04939 | -0.038016 | 3.1891
4664 | 344 | 13.5581 | 0 | 0 | 0 | 14.9069 | 4.5434 | 3.822 | 15.0149 | 2.607 | -0.013569 | -0.013359 | -0.038016 | -0.033896 | 2.6685
4669 | 349 | 13.3782 | 0 | 0 | 0 | 14.7957 | 4.5095 | 3.7881 | 15.0015 | 2.5936 | -0.013359 | -0.013155 | -0.033896 | -0.031232 | 2.4551
4674 | 354 | 13.2034 | 0 | 0 | 0 | 14.6932 | 4.4783 | 3.7569 | 15.0015 | 2.5805 | -0.013155 | -0.012956 | -0.031232 | -0.03001 | 2.345
4679 | 359 | 13.0334 | 0 | 0 | 0 | 14.5947 | 4.4483 | 3.7269 | 14.9856 | 2.5675 | -0.012956 | -0.012763 | -0.03001 | -0.026506 | 2.1956
4684 | 364 | 12.8681 | 0 | 0 | 0 | 14.5078 | 4.4217 | 3.7004 | 14.9824 | 2.5548 | -0.012763 | -0.012576 | -0.026506 | -0.02761 | 2.1365
4689 | 369 | 12.7073 | 0 | 0 | 0 | 14.4172 | 4.3941 | 3.6728 | 14.9816 | 2.5422 | -0.012576 | -0.012393 | -0.02761 | -0.022716 | 2.0129 | -0.094424 | -0.084885 | -0.17491 | -0.14849 | 1.7981
4694 | 374 | 12.5508 | 0 | 0 | 0 | 14.3426 | 4.3714 | 3.6501 | 14.9745 | 2.5298 | -0.012393 | -0.012216 | -0.022716 | -0.024806 | 1.9325
4699 | 379 | 12.3984 | 0 | 0 | 0 | 14.2612 | 4.3466 | 3.6252 | 14.9779 | 2.5176 | -0.012216 | -0.012043 | -0.024806 | -0.021682 | 1.9147
4704 | 384 | 12.25 | 0 | 0 | 0 | 14.1901 | 4.3249 | 3.6036 | 14.9775 | 2.5055 | -0.012043 | -0.011874 | -0.021682 | -0.024508 | 1.9331
4709 | 389 | 12.1054 | 0 | 0 | 0 | 14.1097 | 4.3004 | 3.5791 | 14.9818 | 2.4937 | -0.011874 | -0.01171 | -0.024508 | -0.021406 | 1.9451
4714 | 394 | 11.9645 | 0 | 0 | 0 | 14.0395 | 4.279 | 3.5576 | 14.9709 | 2.4819 | -0.01171 | -0.01155 | -0.021406 | -0.019902 | 1.7751
4719 | 399 | 11.8271 | 0 | 0 | 0 | 13.9742 | 4.2591 | 3.5377 | 14.9672 | 2.4704 | -0.01155 | -0.011394 | -0.019902 | -0.0184 | 1.6686
4724 | 404 | 11.6931 | 0 | 0 | 0 | 13.9138 | 4.2407 | 3.5193 | 14.97 | 2.459 | -0.011394 | -0.011242 | -0.0184 | -0.021494 | 1.7643
4729 | 409 | 11.5623 | 0 | 0 | 0 | 13.8433 | 4.2192 | 3.4979 | 14.9691 | 2.4478 | -0.011242 | -0.011094 | -0.021494 | -0.020802 | 1.8933 | -0.084885 | -0.076987 | -0.14849 | -0.12888 | 1.7098
4734 | 414 | 11.4348 | 0 | 0 | 0 | 13.775 | 4.1984 | 3.4771 | 14.9704 | 2.4367 | -0.011094 | -0.010949 | -0.020802 | -0.015888 | 1.6617
4739 | 419 | 11.3103 | 0 | 0 | 0 | 13.7229 | 4.1825 | 3.4612 | 14.9674 | 2.4257 | -0.010949 | -0.010808 | -0.015888 | -0.020488 | 1.6748
4744 | 424 | 11.1887 | 0 | 0 | 0 | 13.6557 | 4.162 | 3.4407 | 14.9738 | 2.4149 | -0.010808 | -0.01067 | -0.020488 | -0.020598 | 1.9132
4749 | 429 | 11.0699 | 0 | 0 | 0 | 13.5881 | 4.1414 | 3.4201 | 14.9725 | 2.4042 | -0.01067 | -0.010535 | -0.020598 | -0.014604 | 1.6566
4754 | 434 | 10.9539 | 0 | 0 | 0 | 13.5402 | 4.1268 | 3.4055 | 14.972 | 2.3937 | -0.010535 | -0.010404 | -0.014604 | -0.021516 | 1.7293
4759 | 439 | 10.8405 | 0 | 0 | 0 | 13.4696 | 4.1053 | 3.384 | 14.9737 | 2.3833 | -0.010404 | -0.010275 | -0.021516 | -0.016384 | 1.8299
4764 | 444 | 10.7297 | 0 | 0 | 0 | 13.4158 | 4.0889 | 3.3676 | 14.9761 | 2.373 | -0.010275 | -0.010149 | -0.016384 | -0.018206 | 1.6948
4769 | 449 | 10.6214 | 0 | 0 | 0 | 13.3561 | 4.0707 | 3.3494 | 14.9743 | 2.3629 | -0.010149 | -0.010026 | -0.018206 | -0.017632 | 1.7761 | -0.076987 | -0.070343 | -0.12888 | -0.1169 | 1.6677
4774 | 454 | 10.5154 | 0 | 0 | 0 | 13.2982 | 4.0531 | 3.3317 | 14.9795 | 2.3528 | -0.010026 | -0.0099062 | -0.017632 | -0.014304 | 1.6003
4779 | 459 | 10.4118 | 0 | 0 | 0 | 13.2513 | 4.0388 | 3.3174 | 14.979 | 2.3429 | -0.0099062 | -0.0097886 | -0.014304 | -0.015926 | 1.536
4784 | 464 | 10.3103 | 0 | 0 | 0 | 13.1991 | 4.0229 | 3.3015 | 14.979 | 2.3331 | -0.0097886 | -0.0096736 | -0.015926 | -0.017606 | 1.724
4789 | 469 | 10.2111 | 0 | 0 | 0 | 13.1413 | 4.0053 | 3.2839 | 14.9813 | 2.3235 | -0.0096736 | -0.009561 | -0.017606 | -0.016886 | 1.7929
4794 | 474 | 10.1139 | 0 | 0 | 0 | 13.0859 | 3.9884 | 3.267 | 14.9818 | 2.3139 | -0.009561 | -0.0094508 | -0.016886 | -0.014122 | 1.6294
4799 | 479 | 10.0188 | 0 | 0 | 0 | 13.0396 | 3.9743 | 3.2529 | 14.9849 | 2.3045 | -0.0094508 | -0.009343 | -0.014122 | -0.019 | 1.7655
4804 | 484 | 9.9256 | 0 | 0 | 0 | 12.9772 | 3.9553 | 3.2339 | 14.9849 | 2.2951 | -0.009343 | -0.0092373 | -0.019 | -0.013406 | 1.7408
4809 | 489 | 9.8344 | 0 | 0 | 0 | 12.9332 | 3.9419 | 3.2205 | 14.9872 | 2.2859 | -0.0092373 | -0.0091339 | -0.013406 | -0.015104 | 1.553 | -0.070343 | -0.064677 | -0.1169 | -0.10569 | 1.6474
4814 | 494 | 9.7449 | 0 | 0 | 0 | 12.8837 | 3.9268 | 3.2054 | 14.9816 | 2.2767 | -0.0091339 | -0.0090325 | -0.015104 | -0.014902 | 1.6517
4819 | 499 | 9.6573 | 0 | 0 | 0 | 12.8348 | 3.9119 | 3.1905 | 14.9908 | 2.2677 | -0.0090325 | -0.0089332 | -0.014902 | -0.013214 | 1.564
4824 | 504 | 9.5714 | 0 | 0 | 0 | 12.7914 | 3.8986 | 3.1773 | 14.9957 | 2.2588 | -0.0089332 | -0.0088358 | -0.013214 | -0.015024 | 1.5904
4829 | 509 | 9.4872 | 0 | 0 | 0 | 12.7421 | 3.8836 | 3.1622 | 14.9947 | 2.2499 | -0.0088358 | -0.0087404 | -0.015024 | -0.014592 | 1.6848
4834 | 514 | 9.4047 | 0 | 0 | 0 | 12.6943 | 3.869 | 3.1477 | 14.9914 | 2.2412 | -0.0087404 | -0.0086468 | -0.014592 | -0.017592 | 1.853
4839 | 519 | 9.3237 | 0 | 0 | 0 | 12.6365 | 3.8514 | 3.1301 | 14.9905 | 2.2326 | -0.0086468 | -0.0085551 | -0.017592 | -0.01307 | 1.7798
4844 | 524 | 9.2443 | 0 | 0 | 0 | 12.5937 | 3.8384 | 3.117 | 14.9938 | 2.224 | -0.0085551 | -0.0084651 | -0.01307 | -0.0134 | 1.5555
4849 | 529 | 9.1664 | 0 | 0 | 0 | 12.5497 | 3.825 | 3.1036 | 14.9926 | 2.2155 | -0.0084651 | -0.0083768 | -0.0134 | -0.011988 | 1.5066 | -0.064677 | -0.059789 | -0.10569 | -0.095461 | 1.6146
4854 | 534 | 9.0899 | 0 | 0 | 0 | 12.5104 | 3.813 | 3.0916 | 15.001 | 2.2072 | -0.0083768 | -0.0082902 | -0.011988 | -0.014284 | 1.5778
4859 | 539 | 9.0148 | 0 | 0 | 0 | 12.4635 | 3.7987 | 3.0773 | 15.0053 | 2.1989 | -0.0082902 | -0.0082052 | -0.014284 | -0.0144 | 1.7391
4864 | 544 | 8.9412 | 0 | 0 | 0 | 12.4162 | 3.7843 | 3.0629 | 15.0074 | 2.1907 | -0.0082052 | -0.0081218 | -0.0144 | -0.0137 | 1.7207
4869 | 549 | 8.8689 | 0 | 0 | 0 | 12.3713 | 3.7706 | 3.0492 | 15.0148 | 2.1825 | -0.0081218 | -0.0080399 | -0.0137 | -0.0099118 | 1.4587
4874 | 554 | 8.7978 | 0 | 0 | 0 | 12.3388 | 3.7607 | 3.0393 | 15.0115 | 2.1745 | -0.0080399 | -0.0079595 | -0.0099118 | -0.013888 | 1.4901
4879 | 559 | 8.7281 | 0 | 0 | 0 | 12.2932 | 3.7468 | 3.0254 | 15.0166 | 2.1665 | -0.0079595 | -0.0078805 | -0.013888 | -0.01202 | 1.6345
4884 | 564 | 8.6596 | 0 | 0 | 0 | 12.2538 | 3.7348 | 3.0134 | 15.0217 | 2.1587 | -0.0078805 | -0.007803 | -0.01202 | -0.015494 | 1.7566
4889 | 569 | 8.5923 | 0 | 0 | 0 | 12.2029 | 3.7193 | 2.9979 | 15.0118 | 2.1509 | -0.007803 | -0.0077268 | -0.015494 | -0.011396 | 1.729 | -0.059789 | -0.055532 | -0.095461 | -0.092688 | 1.6342
4894 | 574 | 8.5261 | 0 | 0 | 0 | 12.1655 | 3.7079 | 2.9865 | 15.0178 | 2.1431 | -0.0077268 | -0.0076519 | -0.011396 | -0.015776 | 1.7697
4899 | 579 | 8.4611 | 0 | 0 | 0 | 12.1138 | 3.6921 | 2.9707 | 15.0147 | 2.1355 | -0.0076519 | -0.0075784 | -0.015776 | -0.0093842 | 1.648
4904 | 584 | 8.3973 | 0 | 0 | 0 | 12.083 | 3.6827 | 2.9613 | 15.0233 | 2.1279 | -0.0075784 | -0.0075061 | -0.0093842 | -0.01279 | 1.4722
4909 | 589 | 8.3345 | 0 | 0 | 0 | 12.041 | 3.6699 | 2.9486 | 15.0238 | 2.1204 | -0.0075061 | -0.0074351 | -0.01279 | -0.010004 | 1.5239
4914 | 594 | 8.2727 | 0 | 0 | 0 | 12.0082 | 3.6599 | 2.9386 | 15.0263 | 2.113 | -0.0074351 | -0.0073653 | -0.010004 | -0.015304 | 1.7134
4919 | 599 | 8.212 | 0 | 0 | 0 | 11.958 | 3.6446 | 2.9232 | 15.0284 | 2.1056 | -0.0073653 | -0.0072966 | -0.015304 | -0.01369 | 1.9766
4924 | 604 | 8.1523 | 0 | 0 | 0 | 11.9131 | 3.6309 | 2.9096 | 15.0321 | 2.0983 | -0.0072966 | -0.0072292 | -0.01369 | -0.0071158 | 1.4282
4929 | 609 | 8.0936 | 0 | 0 | 0 | 11.8897 | 3.6238 | 2.9024 | 15.0441 | 2.0911 | -0.0072292 | -0.0071628 | -0.0071158 | -0.012014 | 1.3324 | -0.055532 | -0.051791 | -0.092688 | -0.081253 | 1.6172
4934 | 614 | 8.0358 | 0 | 0 | 0 | 11.8503 | 3.6118 | 2.8904 | 15.0427 | 2.0839 | -0.0071628 | -0.0070975 | -0.012014 | -0.014502 | 1.8611
4939 | 619 | 7.979 | 0 | 0 | 0 | 11.8027 | 3.5973 | 2.8759 | 15.0452 | 2.0768 | -0.0070975 | -0.0070333 | -0.014502 | -0.010204 | 1.7457
4944 | 624 | 7.9231 | 0 | 0 | 0 | 11.7692 | 3.5871 | 2.8657 | 15.0423 | 2.0698 | -0.0070333 | -0.0069701 | -0.010204 | -0.0082921 | 1.3197
4949 | 629 | 7.868 | 0 | 0 | 0 | 11.742 | 3.5788 | 2.8574 | 15.0502 | 2.0628 | -0.0069701 | -0.0069079 | -0.0082921 | -0.015218 | 1.6986
4954 | 634 | 7.8139 | 0 | 0 | 0 | 11.6921 | 3.5636 | 2.8422 | 15.0422 | 2.0559 | -0.0069079 | -0.0068467 | -0.015218 | -0.009198 | 1.7713
4959 | 639 | 7.7606 | 0 | 0 | 0 | 11.6619 | 3.5544 | 2.833 | 15.0528 | 2.0491 | -0.0068467 | -0.0067865 | -0.009198 | -0.0097724 | 1.3919
4964 | 644 | 7.7081 | 0 | 0 | 0 | 11.6299 | 3.5446 | 2.8232 | 15.0547 | 2.0423 | -0.0067865 | -0.0067272 | -0.0097724 | -0.013488 | 1.7237
4969 | 649 | 7.6564 | 0 | 0 | 0 | 11.5856 | 3.5311 | 2.8098 | 15.0566 | 2.0355 | -0.0067272 | -0.0066689 | -0.013488 | -0.012704 | 1.9548 | -0.051791 | -0.048479 | -0.081253 | -0.075732 | 1.5654
4974 | 654 | 7.6055 | 0 | 0 | 0 | 11.5439 | 3.5184 | 2.797 | 15.0551 | 2.0289 | -0.0066689 | -0.0066115 | -0.012704 | -0.0075822 | 1.5243
4979 | 659 | 7.5554 | 0 | 0 | 0 | 11.5191 | 3.5108 | 2.7895 | 15.0582 | 2.0223 | -0.0066115 | -0.0065549 | -0.0075822 | -0.0081158 | 1.1927
4984 | 664 | 7.506 | 0 | 0 | 0 | 11.4924 | 3.5027 | 2.7814 | 15.0638 | 2.0157 | -0.0065549 | -0.0064992 | -0.0081158 | -0.010706 | 1.4436
4989 | 669 | 7.4574 | 0 | 0 | 0 | 11.4573 | 3.492 | 2.7706 | 15.0604 | 2.0092 | -0.0064992 | -0.0064443 | -0.010706 | -0.013818 | 1.8968
4994 | 674 | 7.4095 | 0 | 0 | 0 | 11.412 | 3.4782 | 2.7568 | 15.0574 | 2.0028 | -0.0064443 | -0.0063903 | -0.013818 | -0.0092099 | 1.7912
4999 | 679 | 7.3623 | 0 | 0 | 0 | 11.3817 | 3.469 | 2.7476 | 15.0564 | 1.9964 | -0.0063903 | -0.0063371 | -0.0092099 | -0.0097079 | 1.4868
5004 | 684 | 7.3158 | 0 | 0 | 0 | 11.3499 | 3.4593 | 2.7379 | 15.0607 | 1.99 | -0.0063371 | -0.0062847 | -0.0097079 | -0.0094099 | 1.5145
5009 | 689 | 7.27 | 0 | 0 | 0 | 11.319 | 3.4499 | 2.7285 | 15.0616 | 1.9838 | -0.0062847 | -0.006233 | -0.0094099 | -0.008198 | 1.4059 | -0.048479 | -0.045526 | -0.075732 | -0.076736 | 1.6258
5014 | 694 | 7.2248 | 0 | 0 | 0 | 11.2921 | 3.4417 | 2.7203 | 15.067 | 1.9775 | -0.006233 | -0.0061821 | -0.008198 | -0.010104 | 1.4755
5019 | 699 | 7.1803 | 0 | 0 | 0 | 11.259 | 3.4316 | 2.7102 | 15.073 | 1.9713 | -0.0061821 | -0.0061319 | -0.010104 | -0.011506 | 1.7559
5024 | 704 | 7.1364 | 0 | 0 | 0 | 11.2212 | 3.4201 | 2.6987 | 15.0745 | 1.9652 | -0.0061319 | -0.0060824 | -0.011506 | -0.010098 | 1.7679
5029 | 709 | 7.0931 | 0 | 0 | 0 | 11.1881 | 3.41 | 2.6886 | 15.0737 | 1.9591 | -0.0060824 | -0.0060337 | -0.010098 | -0.01031 | 1.6846
5034 | 714 | 7.0504 | 0 | 0 | 0 | 11.1543 | 3.3997 | 2.6783 | 15.0735 | 1.9531 | -0.0060337 | -0.0059856 | -0.01031 | -0.0078099 | 1.5059
5039 | 719 | 7.0083 | 0 | 0 | 0 | 11.1286 | 3.3918 | 2.6705 | 15.0819 | 1.9471 | -0.0059856 | -0.0059383 | -0.0078099 | -0.010406 | 1.5294
5044 | 724 | 6.9669 | 0 | 0 | 0 | 11.0945 | 3.3814 | 2.6601 | 15.0789 | 1.9412 | -0.0059383 | -0.0058916 | -0.010406 | -0.0073 | 1.4947
5049 | 729 | 6.9259 | 0 | 0 | 0 | 11.0705 | 3.3741 | 2.6528 | 15.087 | 1.9353 | -0.0058916 | -0.0058455 | -0.0073 | -0.014916 | 1.8979 | -0.045526 | -0.042879 | -0.076736 | -0.07043 | 1.6634
5054 | 734 | 6.8856 | 0 | 0 | 0 | 11.0216 | 3.3592 | 2.6379 | 15.09 | 1.9294 | -0.0058455 | -0.0058001 | -0.014916 | -0.0057862 | 1.7716
5059 | 739 | 6.8457 | 0 | 0 | 0 | 11.0026 | 3.3534 | 2.6321 | 15.0858 | 1.9236 | -0.0058001 | -0.0057553 | -0.0057862 | -0.0086138 | 1.2481
5064 | 744 | 6.8065 | 0 | 0 | 0 | 10.9744 | 3.3448 | 2.6235 | 15.0834 | 1.9179 | -0.0057553 | -0.0057111 | -0.0086138 | -0.0094178 | 1.5732
5069 | 749 | 6.7677 | 0 | 0 | 0 | 10.9435 | 3.3354 | 2.614 | 15.0947 | 1.9122 | -0.0057111 | -0.0056675 | -0.0094178 | -0.006496 | 1.3967
5074 | 754 | 6.7294 | 0 | 0 | 0 | 10.9221 | 3.3289 | 2.6075 | 15.0978 | 1.9065 | -0.0056675 | -0.0056245 | -0.006496 | -0.011572 | 1.6036
5079 | 759 | 6.6917 | 0 | 0 | 0 | 10.8842 | 3.3173 | 2.596 | 15.098 | 1.9009 | -0.0056245 | -0.0055821 | -0.011572 | -0.0076197 | 1.71
5084 | 764 | 6.6545 | 0 | 0 | 0 | 10.8592 | 3.3097 | 2.5883 | 15.1005 | 1.8953 | -0.0055821 | -0.0055402 | -0.0076197 | -0.012314 | 1.7955
5089 | 769 | 6.6177 | 0 | 0 | 0 | 10.8188 | 3.2974 | 2.576 | 15.0966 | 1.8897 | -0.0055402 | -0.0054989 | -0.012314 | -0.007204 | 1.7646 | -0.042879 | -0.040492 | -0.07043 | -0.063788 | 1.608
5094 | 774 | 6.5814 | 0 | 0 | 0 | 10.7951 | 3.2902 | 2.5688 | 15.1034 | 1.8842 | -0.0054989 | -0.0054581 | -0.007204 | -0.010086 | 1.58
5099 | 779 | 6.5456 | 0 | 0 | 0 | 10.7621 | 3.2801 | 2.5587 | 15.1018 | 1.8788 | -0.0054581 | -0.0054179 | -0.010086 | -0.0066178 | 1.5335
5104 | 784 | 6.5102 | 0 | 0 | 0 | 10.7403 | 3.2735 | 2.5521 | 15.1007 | 1.8734 | -0.0054179 | -0.0053782 | -0.0066178 | -0.0079 | 1.3456
5109 | 789 | 6.4753 | 0 | 0 | 0 | 10.7144 | 3.2656 | 2.5442 | 15.1079 | 1.868 | -0.0053782 | -0.005339 | -0.0079 | -0.0097941 | 1.6523
5114 | 794 | 6.4408 | 0 | 0 | 0 | 10.6823 | 3.2558 | 2.5344 | 15.1089 | 1.8627 | -0.005339 | -0.0053003 | -0.0097941 | -0.0076158 | 1.6349
5119 | 799 | 6.4068 | 0 | 0 | 0 | 10.6573 | 3.2482 | 2.5268 | 15.1074 | 1.8574 | -0.0053003 | -0.005262 | -0.0076158 | -0.0089901 | 1.5732
5124 | 804 | 6.3731 | 0 | 0 | 0 | 10.6278 | 3.2392 | 2.5178 | 15.1042 | 1.8521 | -0.005262 | -0.0052243 | -0.0089901 | -0.012222 | 2.0251
5129 | 809 | 6.3399 | 0 | 0 | 0 | 10.5877 | 3.227 | 2.5056 | 15.1059 | 1.8469 | -0.0052243 | -0.0051871 | -0.012222 | -0.0046882 | 1.619 | -0.040492 | -0.038329 | -0.063788 | -0.066306 | 1.6547
5134 | 814 | 6.3071 | 0 | 0 | 0 | 10.5723 | 3.2223 | 2.5009 | 15.1063 | 1.8417 | -0.0051871 | -0.0051503 | -0.0046882 | -0.0092039 | 1.347
5139 | 819 | 6.2747 | 0 | 0 | 0 | 10.5421 | 3.2131 | 2.4917 | 15.1133 | 1.8365 | -0.0051503 | -0.005114 | -0.0092039 | -0.0091 | 1.7832
5144 | 824 | 6.2427 | 0 | 0 | 0 | 10.5123 | 3.204 | 2.4826 | 15.1187 | 1.8314 | -0.005114 | -0.0050781 | -0.0091 | -0.0096059 | 1.8357
5149 | 829 | 6.2111 | 0 | 0 | 0 | 10.4807 | 3.1944 | 2.473 | 15.1149 | 1.8263 | -0.0050781 | -0.0050427 | -0.0096059 | -0.006698 | 1.609
5154 | 834 | 6.1799 | 0 | 0 | 0 | 10.4588 | 3.1877 | 2.4663 | 15.1165 | 1.8213 | -0.0050427 | -0.0050077 | -0.006698 | -0.010406 | 1.7044
5159 | 839 | 6.149 | 0 | 0 | 0 | 10.4246 | 3.1773 | 2.4559 | 15.1145 | 1.8163 | -0.0050077 | -0.0049731 | -0.010406 | -0.0070803 | 1.7497
5164 | 844 | 6.1185 | 0 | 0 | 0 | 10.4014 | 3.1702 | 2.4488 | 15.1159 | 1.8113 | -0.0049731 | -0.0049389 | -0.0070803 | -0.0070059 | 1.4211
5169 | 849 | 6.0883 | 0 | 0 | 0 | 10.3784 | 3.1632 | 2.4418 | 15.1194 | 1.8064 | -0.0049389 | -0.0049052 | -0.0070059 | -0.01022 | 1.7521 | -0.038329 | -0.036362 | -0.066306 | -0.062912 | 1.73
5174 | 854 | 6.0585 | 0 | 0 | 0 | 10.3449 | 3.153 | 2.4316 | 15.1207 | 1.8015 | -0.0049052 | -0.0048718 | -0.01022 | -0.007898 | 1.8515
5179 | 859 | 6.0291 | 0 | 0 | 0 | 10.319 | 3.1451 | 2.4237 | 15.1201 | 1.7966 | -0.0048718 | -0.0048389 | -0.007898 | -0.008498 | 1.6889
5184 | 864 | 6 | 0 | 0 | 0 | 10.2911 | 3.1366 | 2.4152 | 15.112 | 1.7918 | -0.0048389 | -0.0048063 | -0.008498 | -0.0093941 | 1.8557
5189 | 869 | 5.9712 | 0 | 0 | 0 | 10.2603 | 3.1272 | 2.4058 | 15.1201 | 1.787 | -0.0048063 | -0.0047741 | -0.0093941 | -0.0054961 | 1.5515
5194 | 874 | 5.9428 | 0 | 0 | 0 | 10.2422 | 3.1217 | 2.4003 | 15.1279 | 1.7822 | -0.0047741 | -0.0047423 | -0.0054961 | -0.008696 | 1.4936
5199 | 879 | 5.9147 | 0 | 0 | 0 | 10.2137 | 3.113 | 2.3916 | 15.1178 | 1.7774 | -0.0047423 | -0.0047109 | -0.008696 | -0.005804 | 1.5319
5204 | 884 | 5.8869 | 0 | 0 | 0 | 10.1947 | 3.1072 | 2.3858 | 15.1308 | 1.7727 | -0.0047109 | -0.0046798 | -0.005804 | -0.0103 | 1.7181
5209 | 889 | 5.8594 | 0 | 0 | 0 | 10.1609 | 3.0969 | 2.3755 | 15.1241 | 1.768 | -0.0046798 | -0.0046491 | -0.0103 | -0.008602 | 2.025 | -0.036362 | -0.034564 | -0.062912 | -0.058792 | 1.7152
5214 | 894 | 5.8322 | 0 | 0 | 0 | 10.1326 | 3.0883 | 2.3669 | 15.1224 | 1.7634 | -0.0046491 | -0.0046188 | -0.008602 | -0.0068921 | 1.6706
5219 | 899 | 5.8053 | 0 | 0 | 0 | 10.11 | 3.0814 | 2.36 | 15.1315 | 1.7588 | -0.0046188 | -0.0045887 | -0.0068921 | -0.0095197 | 1.7843
5224 | 904 | 5.7788 | 0 | 0 | 0 | 10.0788 | 3.0719 | 2.3505 | 15.1287 | 1.7542 | -0.0045887 | -0.0045591 | -0.0095197 | -0.0061099 | 1.7062
5229 | 909 | 5.7525 | 0 | 0 | 0 | 10.0587 | 3.0658 | 2.3444 | 15.1393 | 1.7496 | -0.0045591 | -0.0045297 | -0.0061099 | -0.0089039 | 1.6539
5234 | 914 | 5.7265 | 0 | 0 | 0 | 10.0295 | 3.0569 | 2.3355 | 15.1456 | 1.7451 | -0.0045297 | -0.0045007 | -0.0089039 | -0.007802 | 1.8492
5239 | 919 | 5.7008 | 0 | 0 | 0 | 10.0039 | 3.049 | 2.3277 | 15.1497 | 1.7406 | -0.0045007 | -0.004472 | -0.007802 | -0.0067882 | 1.6254
5244 | 924 | 5.6753 | 0 | 0 | 0 | 9.9817 | 3.0423 | 2.3209 | 15.1504 | 1.7361 | -0.004472 | -0.0044437 | -0.0067882 | -0.0082941 | 1.6928
5249 | 929 | 5.6502 | 0 | 0 | 0 | 9.9544 | 3.034 | 2.3126 | 15.1503 | 1.7317 | -0.0044437 | -0.0044156 | -0.0082941 | -0.009998 | 2.066 | -0.034564 | -0.032916 | -0.058792 | -0.059614 | 1.7574
5254 | 934 | 5.6253 | 0 | 0 | 0 | 9.9216 | 3.024 | 2.3026 | 15.1503 | 1.7273 | -0.0044156 | -0.0043878 | -0.009998 | -0.0025079 | 1.4152
5259 | 939 | 5.6006 | 0 | 0 | 0 | 9.9134 | 3.0215 | 2.3001 | 15.1537 | 1.7229 | -0.0043878 | -0.0043604 | -0.0025079 | -0.0091842 | 1.3413
5264 | 944 | 5.5763 | 0 | 0 | 0 | 9.8833 | 3.0123 | 2.2909 | 15.1565 | 1.7185 | -0.0043604 | -0.0043332 | -0.0091842 | -0.0066901 | 1.8242
5269 | 949 | 5.5522 | 0 | 0 | 0 | 9.8613 | 3.0056 | 2.2842 | 15.1637 | 1.7142 | -0.0043332 | -0.0043064 | -0.0066901 | -0.0046921 | 1.316
5274 | 954 | 5.5283 | 0 | 0 | 0 | 9.8459 | 3.0009 | 2.2795 | 15.1667 | 1.7099 | -0.0043064 | -0.0042798 | -0.0046921 | -0.010906 | 1.8212
5279 | 959 | 5.5047 | 0 | 0 | 0 | 9.8102 | 2.99 | 2.2686 | 15.1606 | 1.7056 | -0.0042798 | -0.0042535 | -0.010906 | -0.012308 | 2.7214
5284 | 964 | 5.4813 | 0 | 0 | 0 | 9.7698 | 2.9777 | 2.2563 | 15.1565 | 1.7013 | -0.0042535 | -0.0042275 | -0.012308 | -0.0025059 | 1.7396
5289 | 969 | 5.4582 | 0 | 0 | 0 | 9.7616 | 2.9752 | 2.2538 | 15.1691 | 1.6971 | -0.0042275 | -0.0042018 | -0.0025059 | -0.0071138 | 1.1446 | -0.032916 | -0.0314 | -0.059614 | -0.05613 | 1.7991
5294 | 974 | 5.4353 | 0 | 0 | 0 | 9.7382 | 2.9681 | 2.2467 | 15.162 | 1.6929 | -0.0042018 | -0.0041763 | -0.0071138 | -0.0064901 | 1.6233
5299 | 979 | 5.4127 | 0 | 0 | 0 | 9.7169 | 2.9616 | 2.2402 | 15.1644 | 1.6887 | -0.0041763 | -0.0041511 | -0.0064901 | -0.011702 | 2.1884
5304 | 984 | 5.3902 | 0 | 0 | 0 | 9.6785 | 2.9499 | 2.2285 | 15.1647 | 1.6846 | -0.0041511 | -0.0041262 | -0.011702 | -0.0060941 | 2.1459
5309 | 989 | 5.368 | 0 | 0 | 0 | 9.6585 | 2.9438 | 2.2224 | 15.1731 | 1.6805 | -0.0041262 | -0.0041015 | -0.0060941 | -0.0049 | 1.3354
5314 | 994 | 5.3461 | 0 | 0 | 0 | 9.6424 | 2.9389 | 2.2175 | 15.1736 | 1.6764 | -0.0041015 | -0.0040771 | -0.0049 | -0.0090961 | 1.7144
5319 | 999 | 5.3243 | 0 | 0 | 0 | 9.6126 | 2.9298 | 2.2084 | 15.1727 | 1.6723 | -0.0040771 | -0.0040529 | -0.0090961 | -0.0053079 | 1.769
5324 | 1004 | 5.3028 | 0 | 0 | 0 | 9.5952 | 2.9245 | 2.2031 | 15.1714 | 1.6682 | -0.0040529 | -0.004029 | -0.0053079 | -0.0089099 | 1.7619
5329 | 1009 | 5.2815 | 0 | 0 | 0 | 9.566 | 2.9156 | 2.1942 | 15.1726 | 1.6642 | -0.004029 | -0.0040053 | -0.0089099 | -0.0076 | 2.054 | -0.0314 | -0.03 | -0.05613 | -0.051896 | 1.7581
5334 | 1014 | 5.2604 | 0 | 0 | 0 | 9.541 | 2.908 | 2.1866 | 15.1733 | 1.6602 | -0.0040053 | -0.0039819 | -0.0076 | -0.0079 | 1.9408
5339 | 1019 | 5.2395 | 0 | 0 | 0 | 9.5151 | 2.9001 | 2.1787 | 15.1776 | 1.6562 | -0.0039819 | -0.0039587 | -0.0079 | -0.0070941 | 1.8877
5344 | 1024 | 5.2188 | 0 | 0 | 0 | 9.4918 | 2.893 | 2.1716 | 15.1762 | 1.6523 | -0.0039587 | -0.0039357 | -0.0070941 | -0.001196 | 1.0458
5349 | 1029 | 5.1983 | 0 | 0 | 0 | 9.4879 | 2.8918 | 2.1704 | 15.1789 | 1.6483 | -0.0039357 | -0.003913 | -0.001196 | -0.011098 | 1.5737
5354 | 1034 | 5.1779 | 0 | 0 | 0 | 9.4515 | 2.8807 | 2.1593 | 15.1799 | 1.6444 | -0.003913 | -0.0038905 | -0.011098 | -0.009198 | 2.5995
5359 | 1039 | 5.1578 | 0 | 0 | 0 | 9.4213 | 2.8715 | 2.1501 | 15.1839 | 1.6405 | -0.0038905 | -0.0038682 | -0.009198 | -0.0055197 | 1.8942
5364 | 1044 | 5.1379 | 0 | 0 | 0 | 9.4032 | 2.866 | 2.1446 | 15.1753 | 1.6367 | -0.0038682 | -0.0038461 | -0.0055197 | -0.0065237 | 1.5619
5369 | 1049 | 5.1182 | 0 | 0 | 0 | 9.3818 | 2.8594 | 2.1381 | 15.1737 | 1.6328 | -0.0038461 | -0.0038243 | -0.0065237 | -0.0078 | 1.8684 | -0.03 | -0.028705 | -0.051896 | -0.05587 | 1.8405
5374 | 1054 | 5.0987 | 0 | 0 | 0 | 9.3562 | 2.8516 | 2.1303 | 15.1772 | 1.629 | -0.0038243 | -0.0038026 | -0.0078 | -0.0057118 | 1.7701
5379 | 1059 | 5.0793 | 0 | 0 | 0 | 9.3375 | 2.8459 | 2.1246 | 15.1769 | 1.6252 | -0.0038026 | -0.0037812 | -0.0057118 | -0.0066178 | 1.6265
5384 | 1064 | 5.0602 | 0 | 0 | 0 | 9.3158 | 2.8393 | 2.1179 | 15.1744 | 1.6214 | -0.0037812 | -0.00376 | -0.0066178 | -0.0093921 | 2.1251
5389 | 1069 | 5.0412 | 0 | 0 | 0 | 9.2849 | 2.8299 | 2.1085 | 15.1806 | 1.6176 | -0.00376 | -0.003739 | -0.0093921 | -0.0065941 | 2.1297
5394 | 1074 | 5.0223 | 0 | 0 | 0 | 9.2633 | 2.8233 | 2.1019 | 15.18 | 1.6139 | -0.003739 | -0.0037182 | -0.0065941 | -0.0073645 | 1.8724
5399 | 1079 | 5.0037 | 0 | 0 | 0 | 9.2391 | 2.816 | 2.0946 | 15.178 | 1.6102 | -0.0037182 | -0.0036975 | -0.0073645 | -0.0021059 | 1.2731
5404 | 1084 | 4.9852 | 0 | 0 | 0 | 9.2322 | 2.8138 | 2.0925 | 15.1789 | 1.6065 | -0.0036975 | -0.0036771 | -0.0021059 | -0.0063099 | 1.1443
5409 | 1089 | 4.9669 | 0 | 0 | 0 | 9.2115 | 2.8075 | 2.0862 | 15.1864 | 1.6028 | -0.0036771 | -0.0036569 | -0.0063099 | -0.0083822 | 2.0049 | -0.028705 | -0.027502 | -0.05587 | -0.044876 | 1.7857
5414 | 1094 | 4.9488 | 0 | 0 | 0 | 9.184 | 2.7992 | 2.0778 | 15.1853 | 1.5991 | -0.0036569 | -0.0036369 | -0.0083822 | -0.0073961 | 2.1625
5419 | 1099 | 4.9308 | 0 | 0 | 0 | 9.1598 | 2.7918 | 2.0704 | 15.1886 | 1.5955 | -0.0036369 | -0.003617 | -0.0073961 | -0.006798 | 1.9563
5424 | 1104 | 4.913 | 0 | 0 | 0 | 9.1375 | 2.785 | 2.0636 | 15.1849 | 1.5919 | -0.003617 | -0.0035974 | -0.006798 | -0.0051882 | 1.6602
5429 | 1109 | 4.8954 | 0 | 0 | 0 | 9.1204 | 2.7798 | 2.0584 | 15.1884 | 1.5883 | -0.0035974 | -0.0035779 | -0.0051882 | -0.0073941 | 1.7553
5434 | 1114 | 4.8779 | 0 | 0 | 0 | 9.0962 | 2.7724 | 2.051 | 15.1885 | 1.5847 | -0.0035779 | -0.0035586 | -0.0073941 | -0.0070921 | 2.0297
5439 | 1119 | 4.8606 | 0 | 0 | 0 | 9.0729 | 2.7653 | 2.0439 | 15.1902 | 1.5812 | -0.0035586 | -0.0035395 | -0.0070921 | -0.0068138 | 1.9589
5444 | 1124 | 4.8434 | 0 | 0 | 0 | 9.0505 | 2.7585 | 2.0371 | 15.1995 | 1.5776 | -0.0035395 | -0.0035205 | -0.0068138 | -0.0068059 | 1.9292
5449 | 1129 | 4.8264 | 0 | 0 | 0 | 9.0282 | 2.7517 | 2.0303 | 15.1938 | 1.5741 | -0.0035205 | -0.0035017 | -0.0068059 | -0.0017 | 1.2074 | -0.027502 | -0.026384 | -0.044876 | -0.052276 | 1.8102
5454 | 1134 | 4.8095 | 0 | 0 | 0 | 9.0226 | 2.75 | 2.0286 | 15.199 | 1.5706 | -0.0035017 | -0.0034831 | -0.0017 | -0.0079862 | 1.3915
5459 | 1139 | 4.7928 | 0 | 0 | 0 | 8.9964 | 2.742 | 2.0206 | 15.1975 | 1.5671 | -0.0034831 | -0.0034647 | -0.0079862 | -0.0063921 | 2.0683
5464 | 1144 | 4.7762 | 0 | 0 | 0 | 8.9755 | 2.7356 | 2.0142 | 15.2016 | 1.5637 | -0.0034647 | -0.0034464 | -0.0063921 | -0.0083099 | 2.1288
5469 | 1149 | 4.7598 | 0 | 0 | 0 | 8.9482 | 2.7273 | 2.0059 | 15.2067 | 1.5602 | -0.0034464 | -0.0034283 | -0.0083099 | -0.004998 | 1.9332
5474 | 1154 | 4.7435 | 0 | 0 | 0 | 8.9318 | 2.7223 | 2.0009 | 15.2132 | 1.5568 | -0.0034283 | -0.0034104 | -0.004998 | -0.0052882 | 1.5043
5479 | 1159 | 4.7274 | 0 | 0 | 0 | 8.9144 | 2.717 | 1.9956 | 15.2133 | 1.5534 | -0.0034104 | -0.0033926 | -0.0052882 | -0.0072882 | 1.8502
5484 | 1164 | 4.7113 | 0 | 0 | 0 | 8.8905 | 2.7097 | 1.9883 | 15.2057 | 1.55 | -0.0033926 | -0.003375 | -0.0072882 | -0.0029138 | 1.5041
5489 | 1169 | 4.6955 | 0 | 0 | 0 | 8.881 | 2.7068 | 1.9854 | 15.21 | 1.5466 | -0.003375 | -0.0033575 | -0.0029138 | -0.0080138 | 1.6271 | -0.026384 | -0.025341 | -0.052276 | -0.042804 | 1.8323
5494 | 1174 | 4.6797 | 0 | 0 | 0 | 8.8547 | 2.6988 | 1.9774 | 15.2085 | 1.5432 | -0.0033575 | -0.0033402 | -0.0080138 | -0.006004 | 2.0914
5499 | 1179 | 4.6641 | 0 | 0 | 0 | 8.835 | 2.6928 | 1.9714 | 15.2197 | 1.5399 | -0.0033402 | -0.0033231 | -0.006004 | -0.0083099 | 2.15
5504 | 1184 | 4.6486 | 0 | 0 | 0 | 8.8077 | 2.6845 | 1.9631 | 15.218 | 1.5366 | -0.0033231 | -0.0033061 | -0.0083099 | -0.0057158 | 2.1138
5509 | 1189 | 4.6333 | 0 | 0 | 0 | 8.789 | 2.6787 | 1.9574 | 15.2116 | 1.5333 | -0.0033061 | -0.0032892 | -0.0057158 | -0.006698 | 1.883
5514 | 1194 | 4.6181 | 0 | 0 | 0 | 8.767 | 2.672 | 1.9507 | 15.2125 | 1.53 | -0.0032892 | -0.0032725 | -0.006698 | -0.0058921 | 1.9181
5519 | 1199 | 4.603 | 0 | 0 | 0 | 8.7477 | 2.6662 | 1.9448 | 15.2143 | 1.5267 | -0.0032725 | -0.0032559 | -0.0058921 | -0.0030664 | 1.3701
5524 | 1204 | 4.588 | 0 | 0 | 0 | 8.7376 | 2.6631 | 1.9417 | 15.2226 | 1.5235 | -0.0032559 | -0.0032395 | -0.0030664 | -0.0085763 | 1.7968
5529 | 1209 | 4.5732 | 0 | 0 | 0 | 8.7095 | 2.6545 | 1.9331 | 15.2159 | 1.5202 | -0.0032395 | -0.0032232 | -0.0085763 | -0.0032961 | 1.833 | -0.025341 | -0.024367 | -0.042804 | -0.043297 | 1.7339
5534 | 1214 | 4.5585 | 0 | 0 | 0 | 8.6986 | 2.6512 | 1.9298 | 15.203 | 1.517 | -0.0032232 | -0.0032071 | -0.0032961 | -0.0049 | 1.2759
5539 | 1219 | 4.5439 | 0 | 0 | 0 | 8.6826 | 2.6463 | 1.9249 | 15.2059 | 1.5138 | -0.0032071 | -0.0031911 | -0.0049 | -0.0081099 | 2.0359
5544 | 1224 | 4.5294 | 0 | 0 | 0 | 8.656 | 2.6382 | 1.9168 | 15.2202 | 1.5106 | -0.0031911 | -0.0031752 | -0.0081099 | -0.006302 | 2.2624
5549 | 1229 | 4.5151 | 0 | 0 | 0 | 8.6353 | 2.6319 | 1.9105 | 15.2296 | 1.5074 | -0.0031752 | -0.0031594 | -0.006302 | -0.0029 | 1.45
5554 | 1234 | 4.5008 | 0 | 0 | 0 | 8.6258 | 2.629 | 1.9076 | 15.2216 | 1.5043 | -0.0031594 | -0.0031438 | -0.0029 | -0.0049822 | 1.2522
5559 | 1239 | 4.4867 | 0 | 0 | 0 | 8.6094 | 2.624 | 1.9027 | 15.2117 | 1.5011 | -0.0031438 | -0.0031284 | -0.0049822 | -0.0059197 | 1.7389
5564 | 1244 | 4.4727 | 0 | 0 | 0 | 8.59 | 2.6181 | 1.8967 | 15.2132 | 1.498 | -0.0031284 | -0.003113 | -0.0059197 | -0.0063941 | 1.9733
5569 | 1249 | 4.4588 | 0 | 0 | 0 | 8.569 | 2.6117 | 1.8903 | 15.2068 | 1.4949 | -0.003113 | -0.0030978 | -0.0063941 | -0.0063704 | 2.0552 | -0.024367 | -0.023454 | -0.043297 | -0.041689 | 1.7772
5574 | 1254 | 4.445 | 0 | 0 | 0 | 8.5481 | 2.6053 | 1.884 | 15.2022 | 1.4918 | -0.0030978 | -0.0030827 | -0.0063704 | -0.0021743 | 1.3792
5579 | 1259 | 4.4313 | 0 | 0 | 0 | 8.541 | 2.6032 | 1.8818 | 15.203 | 1.4887 | -0.0030827 | -0.0030677 | -0.0021743 | -0.007502 | 1.5775
5584 | 1264 | 4.4177 | 0 | 0 | 0 | 8.5164 | 2.5957 | 1.8743 | 15.2027 | 1.4856 | -0.0030677 | -0.0030529 | -0.007502 | -0.0058059 | 2.173
5589 | 1269 | 4.4043 | 0 | 0 | 0 | 8.4973 | 2.5899 | 1.8685 | 15.2049 | 1.4826 | -0.0030529 | -0.0030382 | -0.0058059 | -0.0057 | 1.8889
5594 | 1274 | 4.3909 | 0 | 0 | 0 | 8.4786 | 2.5842 | 1.8628 | 15.1988 | 1.4795 | -0.0030382 | -0.0030235 | -0.0057 | -0.0048803 | 1.7448
5599 | 1279 | 4.3776 | 0 | 0 | 0 | 8.4626 | 2.5793 | 1.8579 | 15.1991 | 1.4765 | -0.0030235 | -0.0030091 | -0.0048803 | -0.0048881 | 1.6193
5604 | 1284 | 4.3645 | 0 | 0 | 0 | 8.4466 | 2.5744 | 1.853 | 15.203 | 1.4735 | -0.0030091 | -0.0029947 | -0.0048881 | -0.0059763 | 1.8105
5609 | 1289 | 4.3514 | 0 | 0 | 0 | 8.427 | 2.5684 | 1.847 | 15.2073 | 1.4705 | -0.0029947 | -0.0029804 | -0.0059763 | -0.0051763 | 1.8659 | -0.023454 | -0.022598 | -0.041689 | -0.029045 | 1.5268
5614 | 1294 | 4.3385 | 0 | 0 | 0 | 8.41 | 2.5632 | 1.8419 | 15.2067 | 1.4675 | -0.0029804 | -0.0029663 | -0.0051763 | -0.001896 | 1.1867
5619 | 1299 | 4.3256 | 0 | 0 | 0 | 8.4038 | 2.5613 | 1.84 | 15.2097 | 1.4646 | -0.0029663 | -0.0029523 | -0.001896 | -0.0076079 | 1.6104
5624 | 1304 | 4.3129 | 0 | 0 | 0 | 8.3788 | 2.5537 | 1.8324 | 15.1912 | 1.4616 | -0.0029523 | -0.0029384 | -0.0076079 | -0.006102 | 2.3262
5629 | 1309 | 4.3002 | 0 | 0 | 0 | 8.3588 | 2.5476 | 1.8263 | 15.187 | 1.4587 | -0.0029384 | -0.0029246 | -0.006102 | -0.003902 | 1.7046
5634 | 1314 | 4.2877 | 0 | 0 | 0 | 8.346 | 2.5437 | 1.8224 | 15.1879 | 1.4557 | -0.0029246 | -0.0029109 | -0.003902 | -0.0066434 | 1.8094
5639 | 1319 | 4.2752 | 0 | 0 | 0 | 8.3242 | 2.5371 | 1.8157 | 15.1855 | 1.4528 | -0.0029109 | -0.0028973 | -0.0066434 | -0.0062941 | 2.2272
5644 | 1324 | 4.2628 | 0 | 0 | 0 | 8.3035 | 2.5308 | 1.8094 | 15.2111 | 1.4499 | -0.0028973 | -0.0028838 | -0.0062941 | -0.0040671 | 1.7905
5649 | 1329 | 4.2506 | 0 | 0 | 0 | 8.2902 | 2.5267 | 1.8054 | 15.2159 | 1.4471 | -0.0028838 | -0.0028704 | -0.0040671 | -0.0074454 | 2.0034 | -0.022598 | -0.021793 | -0.029045 | -0.038934 | 1.5405
5654 | 1334 | 4.2384 | 0 | 0 | 0 | 8.2657 | 2.5193 | 1.7979 | 15.2165 | 1.4442 | -0.0028704 | -0.0028572 | -0.0074454 | -0.0023724 | 1.71
5659 | 1339 | 4.2263 | 0 | 0 | 0 | 8.258 | 2.5169 | 1.7955 | 15.2256 | 1.4413 | -0.0028572 | -0.002844 | -0.0023724 | -0.0038526 | 1.0931
5664 | 1344 | 4.2143 | 0 | 0 | 0 | 8.2453 | 2.5131 | 1.7917 | 15.2297 | 1.4385 | -0.002844 | -0.002831 | -0.0038526 | -0.0030526 | 1.2162
5669 | 1349 | 4.2024 | 0 | 0 | 0 | 8.2353 | 2.51 | 1.7886 | 15.2389 | 1.4356 | -0.002831 | -0.002818 | -0.0030526 | -0.0017743 | 0.85346
5674 | 1354 | 4.1905 | 0 | 0 | 0 | 8.2295 | 2.5082 | 1.7869 | 15.244 | 1.4328 | -0.002818 | -0.0028051 | -0.0017743 | -0.0031546 | 0.87768
5679 | 1359 | 4.1788 | 0 | 0 | 0 | 8.2191 | 2.5051 | 1.7837 | 15.2427 | 1.43 | -0.0028051 | -0.0027924 | -0.0031546 | -0.0084487 | 2.0773
5684 | 1364 | 4.1672 | 0 | 0 | 0 | 8.1914 | 2.4966 | 1.7753 | 15.2425 | 1.4272 | -0.0027924 | -0.0027797 | -0.0084487 | 0.0010553 | 1.3191
5689 | 1369 | 4.1556 | 0 | 0 | 0 | 8.1949 | 2.4977 | 1.7763 | 15.2502 | 1.4245 | -0.0027797 | -0.0027671 | 0.0010553 | -0.0042803 | 0.58577 | -0.021793 | -0.021036 | -0.038934 | -0.041643 | 1.8848
5694 | 1374 | 4.1441 | 0 | 0 | 0 | 8.1808 | 2.4934 | 1.772 | 15.2509 | 1.4217 | -0.0027671 | -0.0027547 | -0.0042803 | -0.0045664 | 1.6024
5699 | 1379 | 4.1327 | 0 | 0 | 0 | 8.1659 | 2.4888 | 1.7675 | 15.2545 | 1.4189 | -0.0027547 | -0.0027423 | -0.0045664 | -0.0048941 | 1.7213
5704 | 1384 | 4.1214 | 0 | 0 | 0 | 8.1498 | 2.4839 | 1.7626 | 15.2512 | 1.4162 | -0.0027423 | -0.00273 | -0.0048941 | -3.091e-05 | 0.896
5709 | 1389 | 4.1102 | 0 | 0 | 0 | 8.1497 | 2.4839 | 1.7625 | 15.2576 | 1.4135 | -0.00273 | -0.0027178 | -3.091e-05 | -0.0063355 | 1.1738
5714 | 1394 | 4.099 | 0 | 0 | 0 | 8.1289 | 2.4776 | 1.7562 | 15.2496 | 1.4107 | -0.0027178 | -0.0027057 | -0.0063355 | -0.012882 | 3.5487
5719 | 1399 | 4.0879 | 0 | 0 | 0 | 8.0866 | 2.4647 | 1.7433 | 15.2481 | 1.408 | -0.0027057 | -0.0026937 | -0.012882 | -0.0030842 | 2.9489
5724 | 1404 | 4.0769 | 0 | 0 | 0 | 8.0765 | 2.4616 | 1.7402 | 15.2571 | 1.4053 | -0.0026937 | -0.0026818 | -0.0030842 | -0.0028605 | 1.1057
5729 | 1409 | 4.066 | 0 | 0 | 0 | 8.0671 | 2.4587 | 1.7374 | 15.2586 | 1.4027 | -0.0026818 | -0.00267 | -0.0028605 | -0.0014756 | 0.80909 | -0.021036 | -0.020321 | -0.041643 | -0.030238 | 1.7296
5734 | 1414 | 4.0552 | 0 | 0 | 0 | 8.0623 | 2.4573 | 1.7359 | 15.2643 | 1.4 | -0.00267 | -0.0026582 | -0.0014756 | -0.0025079 | 0.7485
5739 | 1419 | 4.0444 | 0 | 0 | 0 | 8.0541 | 2.4548 | 1.7334 | 15.2621 | 1.3973 | -0.0026582 | -0.0026466 | -0.0025079 | -0.0073474 | 1.8618
5744 | 1424 | 4.0337 | 0 | 0 | 0 | 8.03 | 2.4474 | 1.726 | 15.2589 | 1.3947 | -0.0026466 | -0.002635 | -0.0073474 | -0.0030605 | 1.9671
5749 | 1429 | 4.0231 | 0 | 0 | 0 | 8.0199 | 2.4444 | 1.723 | 15.2579 | 1.3921 | -0.002635 | -0.0026235 | -0.0030605 | -0.012891 | 3.0418
5754 | 1434 | 4.0126 | 0 | 0 | 0 | 7.9776 | 2.4315 | 1.7101 | 15.2517 | 1.3894 | -0.0026235 | -0.0026121 | -0.012891 | 0.001154 | 2.2302
5759 | 1439 | 4.0021 | 0 | 0 | 0 | 7.9814 | 2.4326 | 1.7112 | 15.2646 | 1.3868 | -0.0026121 | -0.0026008 | 0.001154 | -0.0066119 | 1.0535
5764 | 1444 | 3.9917 | 0 | 0 | 0 | 7.9597 | 2.426 | 1.7046 | 15.2589 | 1.3842 | -0.0026008 | -0.0025895 | -0.0066119 | -0.0089026 | 2.9911
5769 | 1449 | 3.9814 | 0 | 0 | 0 | 7.9305 | 2.4171 | 1.6957 | 15.2508 | 1.3816 | -0.0025895 | -0.0025784 | -0.0089026 | 0.0012967 | 1.4632 | -0.020321 | -0.019647 | -0.030238 | -0.034025 | 1.612
5774 | 1454 | 3.9711 | 0 | 0 | 0 | 7.9348 | 2.4184 | 1.697 | 15.2613 | 1.379 | -0.0025784 | -0.0025673 | 0.0012967 | -0.0040257 | 0.53479
5779 | 1459 | 3.9609 | 0 | 0 | 0 | 7.9216 | 2.4144 | 1.693 | 15.2532 | 1.3765 | -0.0025673 | -0.0025563 | -0.0040257 | -0.0076197 | 2.2759
5784 | 1464 | 3.9508 | 0 | 0 | 0 | 7.8966 | 2.4068 | 1.6854 | 15.2601 | 1.3739 | -0.0025563 | -0.0025454 | -0.0076197 | -0.0034434 | 2.165
5789 | 1469 | 3.9408 | 0 | 0 | 0 | 7.8853 | 2.4033 | 1.6819 | 15.2107 | 1.3714 | -0.0025454 | -0.0025346 | -0.0034434 | -0.0017118 | 1.0134
5794 | 1474 | 3.9308 | 0 | 0 | 0 | 7.8796 | 2.4016 | 1.6802 | 15.193 | 1.3688 | -0.0025346 | -0.0025238 | -0.0017118 | -0.0064197 | 1.6115
5799 | 1479 | 3.9209 | 0 | 0 | 0 | 7.8586 | 2.3952 | 1.6738 | 15.1879 | 1.3663 | -0.0025238 | -0.0025131 | -0.0064197 | -0.0051059 | 2.2872
5804 | 1484 | 3.9111 | 0 | 0 | 0 | 7.8418 | 2.3901 | 1.6687 | 15.1917 | 1.3638 | -0.0025131 | -0.0025025 | -0.0051059 | -0.0032079 | 1.656
5809 | 1489 | 3.9013 | 0 | 0 | 0 | 7.8313 | 2.3869 | 1.6655 | 15.1983 | 1.3613 | -0.0025025 | -0.002492 | -0.0032079 | -0.0041664 | 1.4773 | -0.019647 | -0.019009 | -0.034025 | -0.033502 | 1.7474
5814 | 1494 | 3.8916 | 0 | 0 | 0 | 7.8176 | 2.3827 | 1.6613 | 15.2032 | 1.3588 | -0.002492 | -0.0024815 | -0.0041664 | -0.0059882 | 2.0433
5819 | 1499 | 3.8819 | 0 | 0 | 0 | 7.798 | 2.3767 | 1.6553 | 15.2083 | 1.3563 | -0.0024815 | -0.0024711 | -0.0059882 | -0.0022882 | 1.668
5824 | 1504 | 3.8723 | 0 | 0 | 0 | 7.7905 | 2.3744 | 1.6531 | 15.2468 | 1.3539 | -0.0024711 | -0.0024608 | -0.0022882 | -7.23e-06 | 0.46348
5829 | 1509 | 3.8628 | 0 | 0 | 0 | 7.7904 | 2.3744 | 1.653 | 15.3282 | 1.3514 | -0.0024608 | -0.0024506 | -7.23e-06 | -0.0076671 | 1.5691
5834 | 1514 | 3.8534 | 0 | 0 | 0 | 7.7653 | 2.3667 | 1.6454 | 15.3595 | 1.3489 | -0.0024506 | -0.0024404 | -0.0076671 | -0.0014743 | 1.8638
5839 | 1519 | 3.844 | 0 | 0 | 0 | 7.7605 | 2.3653 | 1.6439 | 15.3714 | 1.3465 | -0.0024404 | -0.0024303 | -0.0014743 | -0.0078743 | 1.9248
5844 | 1524 | 3.8346 | 0 | 0 | 0 | 7.7346 | 2.3574 | 1.636 | 15.384 | 1.3441 | -0.0024303 | -0.0024203 | -0.0078743 | -0.0045592 | 2.5605
5849 | 1529 | 3.8254 | 0 | 0 | 0 | 7.7197 | 2.3528 | 1.6315 | 15.4013 | 1.3417 | -0.0024203 | -0.0024103 | -0.0045592 | -0.0060632 | 2.2003 | -0.019009 | -0.018405 | -0.033502 | -0.032568 | 1.766
5854 | 1534 | 3.8162 | 0 | 0 | 0 | 7.6998 | 2.3468 | 1.6254 | 15.4045 | 1.3392 | -0.0024103 | -0.0024004 | -0.0060632 | -0.0015974 | 1.5886
5859 | 1539 | 3.807 | 0 | 0 | 0 | 7.6945 | 2.3452 | 1.6238 | 15.4098 | 1.3368 | -0.0024004 | -0.0023906 | -0.0015974 | -0.0060158 | 1.5929
5864 | 1544 | 3.7979 | 0 | 0 | 0 | 7.6748 | 2.3392 | 1.6178 | 15.4075 | 1.3345 | -0.0023906 | -0.0023808 | -0.0060158 | -0.00089408 | 1.4438
5869 | 1549 | 3.7889 | 0 | 0 | 0 | 7.6719 | 2.3383 | 1.6169 | 15.414 | 1.3321 | -0.0023808 | -0.0023711 | -0.00089408 | -0.0072138 | 1.7117
5874 | 1554 | 3.7799 | 0 | 0 | 0 | 7.6482 | 2.3311 | 1.6097 | 15.4076 | 1.3297 | -0.0023711 | -0.0023615 | -0.0072138 | -0.0040158 | 2.3701
5879 | 1559 | 3.771 | 0 | 0 | 0 | 7.635 | 2.327 | 1.6057 | 15.4053 | 1.3273 | -0.0023615 | -0.0023519 | -0.0040158 | -0.0049158 | 1.8957
5884 | 1564 | 3.7621 | 0 | 0 | 0 | 7.6189 | 2.3221 | 1.6008 | 15.4065 | 1.325 | -0.0023519 | -0.0023424 | -0.0049158 | -0.0027862 | 1.6389
5889 | 1569 | 3.7533 | 0 | 0 | 0 | 7.6097 | 2.3193 | 1.598 | 15.4119 | 1.3226 | -0.0023424 | -0.002333 | -0.0027862 | -0.0067783 | 2.0492 | -0.018405 | -0.017832 | -0.032568 | -0.037768 | 1.9465
5894 | 1574 | 3.7446 | 0 | 0 | 0 | 7.5875 | 2.3126 | 1.5912 | 15.407 | 1.3203 | -0.002333 | -0.0023236 | -0.0067783 | -0.00086644 | 1.6366
5899 | 1579 | 3.7359 | 0 | 0 | 0 | 7.5847 | 2.3117 | 1.5903 | 15.4112 | 1.318 | -0.0023236 | -0.0023143 | -0.00086644 | -0.0080724 | 1.9336
5904 | 1584 | 3.7273 | 0 | 0 | 0 | 7.5582 | 2.3036 | 1.5822 | 15.4176 | 1.3157 | -0.0023143 | -0.0023051 | -0.0080724 | -0.003498 | 2.5008
5909 | 1589 | 3.7187 | 0 | 0 | 0 | 7.5467 | 2.3001 | 1.5788 | 15.415 | 1.3134 | -0.0023051 | -0.0022959 | -0.003498 | -0.004702 | 1.7833
5914 | 1594 | 3.7102 | 0 | 0 | 0 | 7.5313 | 2.2954 | 1.574 | 15.4149 | 1.3111 | -0.0022959 | -0.0022868 | -0.004702 | -0.00029013 | 1.0855
5919 | 1599 | 3.7017 | 0 | 0 | 0 | 7.5303 | 2.2951 | 1.5738 | 15.4178 | 1.3088 | -0.0022868 | -0.0022777 | -0.00029013 | -0.0065434 | 1.5026
5924 | 1604 | 3.6933 | 0 | 0 | 0 | 7.5088 | 2.2886 | 1.5672 | 15.4224 | 1.3065 | -0.0022777 | -0.0022687 | -0.0065434 | -0.0018178 | 1.835
5929 | 1609 | 3.6849 | 0 | 0 | 0 | 7.5029 | 2.2868 | 1.5654 | 15.4158 | 1.3042 | -0.0022687 | -0.0022597 | -0.0018178 | -0.0077039 | 2.1078 | -0.017832 | -0.017289 | -0.037768 | -0.029918 | 1.9212
5934 | 1614 | 3.6766 | 0 | 0 | 0 | 7.4776 | 2.2791 | 1.5577 | 15.4162 | 1.302 | -0.0022597 | -0.0022509 | -0.0077039 | -0.0038862 | 2.5662
5939 | 1619 | 3.6683 | 0 | 0 | 0 | 7.4649 | 2.2752 | 1.5538 | 15.4235 | 1.2997 | -0.0022509 | -0.002242 | -0.0038862 | -0.0022901 | 1.3733
5944 | 1624 | 3.6601 | 0 | 0 | 0 | 7.4573 | 2.2729 | 1.5515 | 15.4163 | 1.2975 | -0.002242 | -0.0022333 | -0.0022901 | -0.0069158 | 2.0611
5949 | 1629 | 3.6519 | 0 | 0 | 0 | 7.4347 | 2.266 | 1.5446 | 15.4242 | 1.2953 | -0.0022333 | -0.0022245 | -0.0069158 | -0.0026842 | 2.1498
5954 | 1634 | 3.6438 | 0 | 0 | 0 | 7.4258 | 2.2633 | 1.5419 | 15.4177 | 1.293 | -0.0022245 | -0.0022159 | -0.0026842 | -0.0039763 | 1.5011
5959 | 1639 | 3.6358 | 0 | 0 | 0 | 7.4128 | 2.2593 | 1.5379 | 15.4149 | 1.2908 | -0.0022159 | -0.0022073 | -0.0039763 | -0.0026158 | 1.4892
5964 | 1644 | 3.6277 | 0 | 0 | 0 | 7.4042 | 2.2567 | 1.5353 | 15.4233 | 1.2886 | -0.0022073 | -0.0021987 | -0.0026158 | -0.007696 | 2.3449
5969 | 1649 | 3.6198 | 0 | 0 | 0 | 7.379 | 2.249 | 1.5276 | 15.417 | 1.2864 | -0.0021987 | -0.0021902 | -0.007696 | -0.0036039 | 2.571 | -0.017289 | -0.016772 | -0.029918 | -0.035255 | 1.9191
5974 | 1654 | 3.6119 | 0 | 0 | 0 | 7.3671 | 2.2454 | 1.524 | 15.4166 | 1.2842 | -0.0021902 | -0.0021818 | -0.0036039 | -0.0020862 | 1.3001
5979 | 1659 | 3.604 | 0 | 0 | 0 | 7.3603 | 2.2433 | 1.5219 | 15.4243 | 1.282 | -0.0021818 | -0.0021734 | -0.0020862 | -0.0063039 | 1.9302
5984 | 1664 | 3.5962 | 0 | 0 | 0 | 7.3396 | 2.237 | 1.5156 | 15.4288 | 1.2799 | -0.0021734 | -0.0021651 | -0.0063039 | -0.0021039 | 1.9343
5989 | 1669 | 3.5884 | 0 | 0 | 0 | 7.3327 | 2.2349 | 1.5135 | 15.4228 | 1.2777 | -0.0021651 | -0.0021568 | -0.0021039 | -0.0078079 | 2.2985
5994 | 1674 | 3.5806 | 0 | 0 | 0 | 7.3071 | 2.2271 | 1.5057 | 15.4216 | 1.2755 | -0.0021568 | -0.0021486 | -0.0078079 | -0.0015941 | 2.1783
5999 | 1679 | 3.573 | 0 | 0 | 0 | 7.3019 | 2.2255 | 1.5041 | 15.4148 | 1.2734 | -0.0021486 | -0.0021404 | -0.0015941 | -0.0036059 | 1.2142
6004 | 1684 | 3.5653 | 0 | 0 | 0 | 7.29 | 2.2219 | 1.5005 | 15.4228 | 1.2713 | -0.0021404 | -0.0021323 | -0.0036059 | -0.0028118 | 1.5013
6009 | 1689 | 3.5577 | 0 | 0 | 0 | 7.2808 | 2.2191 | 1.4977 | 15.4201 | 1.2691 | -0.0021323 | -0.0021242 | -0.0028118 | -0.0056882 | 1.9995 | -0.016772 | -0.01628 | -0.035255 | -0.034743 | 2.1183
6014 | 1694 | 3.5502 | 0 | 0 | 0 | 7.2621 | 2.2134 | 1.492 | 15.4169 | 1.267 | -0.0021242 | -0.0021162 | -0.0056882 | -0.0041882 | 2.3278
6019 | 1699 | 3.5427 | 0 | 0 | 0 | 7.2484 | 2.2092 | 1.4878 | 15.4216 | 1.2649 | -0.0021162 | -0.0021082 | -0.0041882 | -0.0048039 | 2.1292
6024 | 1704 | 3.5352 | 0 | 0 | 0 | 7.2326 | 2.2044 | 1.483 | 15.4583 | 1.2628 | -0.0021082 | -0.0021003 | -0.0048039 | -0.004998 | 2.3293
6029 | 1709 | 3.5278 | 0 | 0 | 0 | 7.2162 | 2.1994 | 1.478 | 15.4674 | 1.2607 | -0.0021003 | -0.0020924 | -0.004998 | -0.0049941 | 2.3832
6034 | 1714 | 3.5204 | 0 | 0 | 0 | 7.1999 | 2.1944 | 1.473 | 15.4722 | 1.2586 | -0.0020924 | -0.0020846 | -0.0049941 | -0.0015842 | 1.5718
6039 | 1719 | 3.5131 | 0 | 0 | 0 | 7.1947 | 2.1928 | 1.4715 | 15.4708 | 1.2565 | -0.0020846 | -0.0020768 | -0.0015842 | -0.0031961 | 1.1502
6044 | 1724 | 3.5058 | 0 | 0 | 0 | 7.1842 | 2.1896 | 1.4683 | 15.4776 | 1.2544 | -0.0020768 | -0.0020691 | -0.0031961 | -0.005802 | 2.1727
6049 | 1729 | 3.4986 | 0 | 0 | 0 | 7.1651 | 2.1838 | 1.4625 | 15.4738 | 1.2523 | -0.0020691 | -0.0020614 | -0.005802 | -0.0022921 | 1.9564 | -0.01628 | -0.015812 | -0.034743 | -0.030236 | 2.0215
6054 | 1734 | 3.4913 | 0 | 0 | 0 | 7.1576 | 2.1815 | 1.4602 | 15.486 | 1.2503 | -0.0020614 | -0.0020538 | -0.0022921 | -0.0042803 | 1.5989
6059 | 1739 | 3.4842 | 0 | 0 | 0 | 7.1436 | 2.1773 | 1.4559 | 15.4942 | 1.2482 | -0.0020538 | -0.0020462 | -0.0042803 | -0.0058882 | 2.4816
6064 | 1744 | 3.4771 | 0 | 0 | 0 | 7.1243 | 2.1714 | 1.45 | 15.489 | 1.2462 | -0.0020462 | -0.0020387 | -0.0058882 | -0.0025901 | 2.0726
6069 | 1749 | 3.47 | 0 | 0 | 0 | 7.1158 | 2.1688 | 1.4474 | 15.4898 | 1.2441 | -0.0020387 | -0.0020312 | -0.0025901 | -0.0056 | 2.0151
6074 | 1754 | 3.4629 | 0 | 0 | 0 | 7.0974 | 2.1632 | 1.4418 | 15.4826 | 1.2421 | -0.0020312 | -0.0020237 | -0.0056 | -0.0032941 | 2.1913
6079 | 1759 | 3.4559 | 0 | 0 | 0 | 7.0866 | 2.1599 | 1.4385 | 15.4839 | 1.2401 | -0.0020237 | -0.0020163 | -0.0032941 | -0.0036079 | 1.7087
6084 | 1764 | 3.449 | 0 | 0 | 0 | 7.0747 | 2.1563 | 1.4349 | 15.4882 | 1.2381 | -0.0020163 | -0.002009 | -0.0036079 | -0.0071901 | 2.6858
6089 | 1769 | 3.4421 | 0 | 0 | 0 | 7.0511 | 2.1491 | 1.4277 | 15.4853 | 1.2361 | -0.002009 | -0.0020017 | -0.0071901 | -0.003404 | 2.6381 | -0.015812 | -0.015366 | -0.030236 | -0.036214 | 2.1377
6094 | 1774 | 3.4352 | 0 | 0 | 0 | 7.04 | 2.1457 | 1.4243 | 15.4844 | 1.2341 | -0.0020017 | -0.0019944 | -0.003404 | -0.0022039 | 1.4023
6099 | 1779 | 3.4283 | 0 | 0 | 0 | 7.0327 | 2.1435 | 1.4221 | 15.4891 | 1.2321 | -0.0019944 | -0.0019872 | -0.0022039 | -0.0078921 | 2.5409
6104 | 1784 | 3.4215 | 0 | 0 | 0 | 7.0069 | 2.1356 | 1.4142 | 15.4846 | 1.2301 | -0.0019872 | -0.00198 | -0.0078921 | -0.0024099 | 2.5918
6109 | 1789 | 3.4148 | 0 | 0 | 0 | 6.9989 | 2.1332 | 1.4118 | 15.4863 | 1.2281 | -0.00198 | -0.0019728 | -0.0024099 | -0.0027059 | 1.2945
6114 | 1794 | 3.408 | 0 | 0 | 0 | 6.9901 | 2.1305 | 1.4091 | 15.4862 | 1.2261 | -0.0019728 | -0.0019657 | -0.0027059 | -0.0033 | 1.5255
6119 | 1799 | 3.4013 | 0 | 0 | 0 | 6.9792 | 2.1272 | 1.4058 | 15.4821 | 1.2242 | -0.0019657 | -0.0019587 | -0.0033 | -0.0055059 | 2.2459
6124 | 1804 | 3.3947 | 0 | 0 | 0 | 6.9612 | 2.1217 | 1.4003 | 15.4963 | 1.2222 | -0.0019587 | -0.0019517 | -0.0055059 | -0.0028138 | 2.1252
6129 | 1809 | 3.3881 | 0 | 0 | 0 | 6.9519 | 2.1188 | 1.3975 | 15.4869 | 1.2203 | -0.0019517 | -0.0019447 | -0.0028138 | -0.0073 | 2.5999 | -0.015366 | -0.01494 | -0.036214 | -0.030316 | 2.1907
6134 | 1814 | 3.3815 | 0 | 0 | 0 | 6.928 | 2.1115 | 1.3902 | 15.4889 | 1.2183 | -0.0019447 | -0.0019378 | -0.0073 | -0.0043901 | 3.0084
6139 | 1819 | 3.3749 | 0 | 0 | 0 | 6.9136 | 2.1072 | 1.3858 | 15.4763 | 1.2164 | -0.0019378 | -0.0019309 | -0.0043901 | -0.0031217 | 1.9406
6144 | 1824 | 3.3684 | 0 | 0 | 0 | 6.9033 | 2.104 | 1.3827 | 15.4872 | 1.2144 | -0.0019309 | -0.001924 | -0.0031217 | -0.0042138 | 1.9039
6149 | 1829 | 3.3619 | 0 | 0 | 0 | 6.8895 | 2.0998 | 1.3785 | 15.4882 | 1.2125 | -0.001924 | -0.0019172 | -0.0042138 | -0.0021961 | 1.6669
6154 | 1834 | 3.3555 | 0 | 0 | 0 | 6.8823 | 2.0976 | 1.3763 | 15.4834 | 1.2106 | -0.0019172 | -0.0019104 | -0.0021961 | -0.005198 | 1.9346
6159 | 1839 | 3.3491 | 0 | 0 | 0 | 6.8653 | 2.0924 | 1.3711 | 15.4699 | 1.2087 | -0.0019104 | -0.0019037 | -0.005198 | -0.0043882 | 2.5126
6164 | 1844 | 3.3427 | 0 | 0 | 0 | 6.8509 | 2.088 | 1.3667 | 15.4901 | 1.2068 | -0.0019037 | -0.001897 | -0.0043882 | -0.0054059 | 2.5779
6169 | 1849 | 3.3364 | 0 | 0 | 0 | 6.8331 | 2.0826 | 1.3613 | 15.4895 | 1.2049 | -0.001897 | -0.0018903 | -0.0054059 | -0.0010158 | 1.6915 | -0.01494 | -0.014533 | -0.030316 | -0.032832 | 2.1458
6174 | 1854 | 3.3301 | 0 | 0 | 0 | 6.8298 | 2.0816 | 1.3602 | 15.4931 | 1.203 | -0.0018903 | -0.0018837 | -0.0010158 | -0.007798 | 2.3417
6179 | 1859 | 3.3238 | 0 | 0 | 0 | 6.8042 | 2.0738 | 1.3525 | 15.49 | 1.2011 | -0.0018837 | -0.0018771 | -0.007798 | -0.0053941 | 3.5055
6184 | 1864 | 3.3176 | 0 | 0 | 0 | 6.7865 | 2.0684 | 1.3471 | 15.4801 | 1.1992 | -0.0018771 | -0.0018706 | -0.0053941 | -0.00078026 | 1.6432
6189 | 1869 | 3.3114 | 0 | 0 | 0 | 6.7839 | 2.0676 | 1.3463 | 15.4877 | 1.1974 | -0.0018706 | -0.0018641 | -0.00078026 | -0.0042 | 1.3367
6194 | 1874 | 3.3052 | 0 | 0 | 0 | 6.7702 | 2.0634 | 1.3421 | 15.4843 | 1.1955 | -0.0018641 | -0.0018576 | -0.0042 | -0.0045138 | 2.3416
6199 | 1879 | 3.2991 | 0 | 0 | 0 | 6.7554 | 2.0589 | 1.3376 | 15.4913 | 1.1936 | -0.0018576 | -0.0018512 | -0.0045138 | -0.0033217 | 2.1116
6204 | 1884 | 3.293 | 0 | 0 | 0 | 6.7445 | 2.0556 | 1.3342 | 15.4759 | 1.1918 | -0.0018512 | -0.0018448 | -0.0033217 | -0.0032921 | 1.7894
6209 | 1889 | 3.2869 | 0 | 0 | 0 | 6.7337 | 2.0523 | 1.3309 | 15.4819 | 1.19 | -0.0018448 | -0.0018384 | -0.0032921 | -0.0056059 | 2.418 | -0.014533 | -0.014143 | -0.032832 | -0.02891 | 2.1502
6214 | 1894 | 3.2809 | 0 | 0 | 0 | 6.7153 | 2.0467 | 1.3253 | 15.481 | 1.1881 | -0.0018384 | -0.0018321 | -0.0056059 | -0.0024059 | 2.1797
6219 | 1899 | 3.2749 | 0 | 0 | 0 | 6.7074 | 2.0443 | 1.3229 | 15.4886 | 1.1863 | -0.0018321 | -0.0018258 | -0.0024059 | -0.00049802 | 0.79208
6224 | 1904 | 3.2689 | 0 | 0 | 0 | 6.7057 | 2.0438 | 1.3224 | 15.4871 | 1.1845 | -0.0018258 | -0.0018196 | -0.00049802 | -0.0059961 | 1.7866
6229 | 1909 | 3.263 | 0 | 0 | 0 | 6.6861 | 2.0378 | 1.3164 | 15.4848 | 1.1826 | -0.0018196 | -0.0018134 | -0.0059961 | -0.005202 | 3.0816
6234 | 1914 | 3.2571 | 0 | 0 | 0 | 6.669 | 2.0326 | 1.3112 | 15.4851 | 1.1808 | -0.0018134 | -0.0018072 | -0.005202 | -0.0042197 | 2.6014
6239 | 1919 | 3.2512 | 0 | 0 | 0 | 6.6552 | 2.0284 | 1.307 | 15.4982 | 1.179 | -0.0018072 | -0.001801 | -0.0042197 | -0.0028217 | 1.9502
6244 | 1924 | 3.2453 | 0 | 0 | 0 | 6.6459 | 2.0256 | 1.3042 | 15.4975 | 1.1772 | -0.001801 | -0.0017949 | -0.0028217 | -0.0060822 | 2.4792
6249 | 1929 | 3.2395 | 0 | 0 | 0 | 6.6259 | 2.0195 | 1.2981 | 15.4947 | 1.1754 | -0.0017949 | -0.0017889 | -0.0060822 | -0.0024079 | 2.3656 | -0.014143 | -0.013771 | -0.02891 | -0.026406 | 1.9799
6254 | 1934 | 3.2337 | 0 | 0 | 0 | 6.618 | 2.0171 | 1.2957 | 15.4865 | 1.1736 | -0.0017889 | -0.0017828 | -0.0024079 | -0.0022059 | 1.2916
6259 | 1939 | 3.228 | 0 | 0 | 0 | 6.6108 | 2.0149 | 1.2935 | 15.4873 | 1.1718 | -0.0017828 | -0.0017768 | -0.0022059 | -0.0026099 | 1.3533
6264 | 1944 | 3.2222 | 0 | 0 | 0 | 6.6022 | 2.0123 | 1.2909 | 15.4947 | 1.1701 | -0.0017768 | -0.0017708 | -0.0026099 | -0.0025 | 1.4403
6269 | 1949 | 3.2165 | 0 | 0 | 0 | 6.594 | 2.0098 | 1.2884 | 15.4784 | 1.1683 | -0.0017708 | -0.0017649 | -0.0025 | -0.0058941 | 2.3773
6274 | 1954 | 3.2108 | 0 | 0 | 0 | 6.5747 | 2.0039 | 1.2825 | 15.4939 | 1.1665 | -0.0017649 | -0.001759 | -0.0058941 | -0.0030079 | 2.5235
6279 | 1959 | 3.2052 | 0 | 0 | 0 | 6.5648 | 2.0009 | 1.2795 | 15.5041 | 1.1648 | -0.001759 | -0.0017531 | -0.0030079 | -0.0044901 | 2.1364
6284 | 1964 | 3.1996 | 0 | 0 | 0 | 6.5501 | 1.9964 | 1.275 | 15.5104 | 1.163 | -0.0017531 | -0.0017472 | -0.0044901 | -0.0057941 | 2.9393
6289 | 1969 | 3.194 | 0 | 0 | 0 | 6.5311 | 1.9906 | 1.2692 | 15.5029 | 1.1613 | -0.0017472 | -0.0017414 | -0.0057941 | 0.00040987 | 1.5374 | -0.013771 | -0.013415 | -0.026406 | -0.029003 | 2.0414
6294 | 1974 | 3.1884 | 0 | 0 | 0 | 6.5324 | 1.991 | 1.2696 | 15.5111 | 1.1595 | -0.0017414 | -0.0017356 | 0.00040987 | -0.0057882 | 1.5527
6299 | 1979 | 3.1829 | 0 | 0 | 0 | 6.5134 | 1.9852 | 1.2638 | 15.5083 | 1.1578 | -0.0017356 | -0.0017299 | -0.0057882 | -0.002998 | 2.5327
6304 | 1984 | 3.1774 | 0 | 0 | 0 | 6.5036 | 1.9822 | 1.2608 | 15.4957 | 1.1561 | -0.0017299 | -0.0017242 | -0.002998 | -0.0001079 | 0.89645
6309 | 1989 | 3.1719 | 0 | 0 | 0 | 6.5032 | 1.9821 | 1.2607 | 15.4979 | 1.1543 | -0.0017242 | -0.0017185 | -0.0001079 | -0.0052099 | 1.5496
6314 | 1994 | 3.1665 | 0 | 0 | 0 | 6.4862 | 1.9769 | 1.2555 | 15.5115 | 1.1526 | -0.0017185 | -0.0017128 | -0.0052099 | -0.0042079 | 2.7437
6319 | 1999 | 3.1611 | 0 | 0 | 0 | 6.4723 | 1.9727 | 1.2513 | 15.5151 | 1.1509 | -0.0017128 | -0.0017072 | -0.0042079 | -0.0036079 | 2.2848
6324 | 2004 | 3.1557 | 0 | 0 | 0 | 6.4605 | 1.9691 | 1.2477 | 15.5076 | 1.1492 | -0.0017072 | -0.0017016 | -0.0036079 | -0.004896 | 2.496
6329 | 2009 | 3.1503 | 0 | 0 | 0 | 6.4444 | 1.9642 | 1.2428 | 15.4961 | 1.1475 | -0.0017016 | -0.001696 | -0.004896 | -0.0016039 | 1.91 | -0.013415 | -0.013073 | -0.029003 | -0.022082 | 1.9226
6334 | 2014 | 3.145 | 0 | 0 | 0 | 6.4392 | 1.9626 | 1.2412 | 15.5029 | 1.1458 | -0.001696 | -0.0016905 | -0.0016039 | -0.0064941 | 2.396
6339 | 2019 | 3.1397 | 0 | 0 | 0 | 6.4179 | 1.9561 | 1.2347 | 15.495 | 1.1441 | -0.0016905 | -0.001685 | -0.0064941 | -0.0030862 | 2.835
6344 | 2024 | 3.1344 | 0 | 0 | 0 | 6.4078 | 1.953 | 1.2316 | 15.4938 | 1.1424 | -0.001685 | -0.0016795 | -0.0030862 | -0.0021803 | 1.5645
6349 | 2029 | 3.1291 | 0 | 0 | 0 | 6.4006 | 1.9508 | 1.2294 | 15.5089 | 1.1408 | -0.0016795 | -0.001674 | -0.0021803 | -0.0035645 | 1.7144
6354 | 2034 | 3.1239 | 0 | 0 | 0 | 6.3889 | 1.9472 | 1.2259 | 15.5028 | 1.1391 | -0.001674 | -0.0016686 | -0.0035645 | -0.0029039 | 1.9345
6359 | 2039 | 3.1187 | 0 | 0 | 0 | 6.3794 | 1.9443 | 1.223 | 15.5084 | 1.1374 | -0.0016686 | -0.0016632 | -0.0029039 | -0.0046882 | 2.2804
6364 | 2044 | 3.1135 | 0 | 0 | 0 | 6.364 | 1.9397 | 1.2183 | 15.5065 | 1.1357 | -0.0016632 | -0.0016578 | -0.0046882 | -0.0044822 | 2.7611
6369 | 2049 | 3.1083 | 0 | 0 | 0 | 6.3493 | 1.9352 | 1.2138 | 15.5037 | 1.1341 | -0.0016578 | -0.0016525 | -0.0044822 | -0.001098 | 1.6824 | -0.013073 | -0.012745 | -0.022082 | -0.023112 | 1.7521
6374 | 2054 | 3.1032 | 0 | 0 | 0 | 6.3457 | 1.9341 | 1.2127 | 15.5116 | 1.1324 | -0.0016525 | -0.0016472 | -0.001098 | -0.0036099 | 1.4292
6379 | 2059 | 3.0981 | 0 | 0 | 0 | 6.3338 | 1.9305 | 1.2091 | 15.4983 | 1.1308 | -0.0016472 | -0.0016419 | -0.0036099 | -0.0018059 | 1.6448
6384 | 2064 | 3.093 | 0 | 0 | 0 | 6.3279 | 1.9287 | 1.2073 | 15.5093 | 1.1291 | -0.0016419 | -0.0016366 | -0.0018059 | -0.0027 | 1.3752
6389 | 2069 | 3.088 | 0 | 0 | 0 | 6.3191 | 1.926 | 1.2046 | 15.5108 | 1.1275 | -0.0016366 | -0.0016314 | -0.0027 | -0.0038961 | 2.0195
6394 | 2074 | 3.0829 | 0 | 0 | 0 | 6.3063 | 1.9221 | 1.2007 | 15.5032 | 1.1259 | -0.0016314 | -0.0016262 | -0.0038961 | -0.003502 | 2.2706
6399 | 2079 | 3.0779 | 0 | 0 | 0 | 6.2948 | 1.9186 | 1.1972 | 15.5059 | 1.1243 | -0.0016262 | -0.001621 | -0.003502 | -0.0023901 | 1.8134
6404 | 2084 | 3.0729 | 0 | 0 | 0 | 6.2869 | 1.9162 | 1.1948 | 15.5207 | 1.1226 | -0.001621 | -0.0016159 | -0.0023901 | -0.0030803 | 1.6907
6409 | 2089 | 3.068 | 0 | 0 | 0 | 6.2768 | 1.9131 | 1.1917 | 15.5153 | 1.121 | -0.0016159 | -0.0016108 | -0.0030803 | -0.0036059 | 2.0727 | -0.012745 | -0.01243 | -0.023112 | -0.0233 | 1.8443
6414 | 2094 | 3.063 | 0 | 0 | 0 | 6.265 | 1.9095 | 1.1881 | 15.5256 | 1.1194 | -0.0016108 | -0.0016057 | -0.0036059 | -0.00019803 | 1.1793
6419 | 2099 | 3.0581 | 0 | 0 | 0 | 6.2644 | 1.9093 | 1.1879 | 15.5346 | 1.1178 | -0.0016057 | -0.0016006 | -0.00019803 | -0.0064099 | 2.067
6424 | 2104 | 3.0532 | 0 | 0 | 0 | 6.2433 | 1.9029 | 1.1815 | 15.539 | 1.1162 | -0.0016006 | -0.0015956 | -0.0064099 | -0.0019901 | 2.6238
6429 | 2109 | 3.0484 | 0 | 0 | 0 | 6.2368 | 1.9009 | 1.1795 | 15.535 | 1.1146 | -0.0015956 | -0.0015906 | -0.0019901 | -0.00058618 | 0.80722
6434 | 2114 | 3.0435 | 0 | 0 | 0 | 6.2349 | 1.9003 | 1.1789 | 15.5301 | 1.113 | -0.0015906 | -0.0015856 | -0.00058618 | -0.0065099 | 2.24
6439 | 2119 | 3.0387 | 0 | 0 | 0 | 6.2135 | 1.8938 | 1.1724 | 15.5319 | 1.1114 | -0.0015856 | -0.0015806 | -0.0065099 | 0.00079211 | 1.7987
6444 | 2124 | 3.0339 | 0 | 0 | 0 | 6.2161 | 1.8946 | 1.1732 | 15.5366 | 1.1098 | -0.0015806 | -0.0015757 | 0.00079211 | -0.004604 | 1.2131
6449 | 2129 | 3.0291 | 0 | 0 | 0 | 6.201 | 1.89 | 1.1686 | 15.5434 | 1.1083 | -0.0015757 | -0.0015708 | -0.004604 | -0.0035 | 2.5745 | -0.01243 | -0.012128 | -0.0233 | -0.019455 | 1.7376
6454 | 2134 | 3.0244 | 0 | 0 | 0 | 6.1895 | 1.8865 | 1.1651 | 15.5433 | 1.1067 | -0.0015708 | -0.0015659 | -0.0035 | -0.0065921 | 3.2206
6459 | 2139 | 3.0196 | 0 | 0 | 0 | 6.1679 | 1.8799 | 1.1585 | 15.5314 | 1.1051 | -0.0015659 | -0.001561 | -0.0065921 | 0.0011921 | 1.7192
6464 | 2144 | 3.0149 | 0 | 0 | 0 | 6.1718 | 1.8811 | 1.1597 | 15.5428 | 1.1036 | -0.001561 | -0.0015562 | 0.0011921 | -0.0035079 | 0.7476
6469 | 2149 | 3.0102 | 0 | 0 | 0 | 6.1603 | 1.8776 | 1.1562 | 15.5702 | 1.102 | -0.0015562 | -0.0015513 | -0.0035079 | -0.0033941 | 2.221
6474 | 2154 | 3.0056 | 0 | 0 | 0 | 6.1492 | 1.8742 | 1.1528 | 15.5737 | 1.1005 | -0.0015513 | -0.0015466 | -0.0033941 | -0.002802 | 1.9995
6479 | 2159 | 3.0009 | 0 | 0 | 0 | 6.14 | 1.8714 | 1.15 | 15.5827 | 1.0989 | -0.0015466 | -0.0015418 | -0.002802 | -0.0035921 | 2.0712
6484 | 2164 | 2.9963 | 0 | 0 | 0 | 6.1282 | 1.8678 | 1.1464 | 15.6056 | 1.0974 | -0.0015418 | -0.001537 | -0.0035921 | -0.001104 | 1.5228
6489 | 2169 | 2.9917 | 0 | 0 | 0 | 6.1246 | 1.8667 | 1.1453 | 15.6286 | 1.0958 | -0.001537 | -0.0015323 | -0.001104 | -0.0033941 | 1.4678 | -0.012128 | -0.011838 | -0.019455 | -0.025 | 1.861
6494 | 2174 | 2.9871 | 0 | 0 | 0 | 6.1134 | 1.8633 | 1.1419 | 15.6347 | 1.0943 | -0.0015323 | -0.0015276 | -0.0033941 | -0.0013882 | 1.5608
6499 | 2179 | 2.9826 | 0 | 0 | 0 | 6.1089 | 1.8619 | 1.1405 | 15.6442 | 1.0928 | -0.0015276 | -0.0015229 | -0.0013882 | -0.0058921 | 2.3911
6504 | 2184 | 2.978 | 0 | 0 | 0 | 6.0895 | 1.856 | 1.1346 | 15.6454 | 1.0913 | -0.0015229 | -0.0015183 | -0.0058921 | 0.0017941 | 1.3398
6509 | 2189 | 2.9735 | 0 | 0 | 0 | 6.0954 | 1.8578 | 1.1364 | 15.6614 | 1.0897 | -0.0015183 | -0.0015137 | 0.0017941 | -0.0056 | 1.2627
6514 | 2194 | 2.969 | 0 | 0 | 0 | 6.077 | 1.8522 | 1.1308 | 15.6583 | 1.0882 | -0.0015137 | -0.0015091 | -0.0056 | -0.0035901 | 3.0383
6519 | 2199 | 2.9645 | 0 | 0 | 0 | 6.0653 | 1.8486 | 1.1272 | 15.6649 | 1.0867 | -0.0015091 | -0.0015045 | -0.0035901 | -0.0028842 | 2.1477
6524 | 2204 | 2.9601 | 0 | 0 | 0 | 6.0558 | 1.8457 | 1.1243 | 15.6572 | 1.0852 | -0.0015045 | -0.0014999 | -0.0028842 | 0.0015 | 0.4563
6529 | 2209 | 2.9556 | 0 | 0 | 0 | 6.0607 | 1.8472 | 1.1258 | 15.6674 | 1.0837 | -0.0014999 | -0.0014954 | 0.0015 | -0.0057197 | 1.4161 | -0.011838 | -0.011559 | -0.025 | -0.020388 | 1.9358
6534 | 2214 | 2.9512 | 0 | 0 | 0 | 6.042 | 1.8415 | 1.1201 | 15.6684 | 1.0822 | -0.0014954 | -0.0014909 | -0.0057197 | -0.0015901 | 2.4437
6539 | 2219 | 2.9468 | 0 | 0 | 0 | 6.0367 | 1.8399 | 1.1185 | 15.677 | 1.0807 | -0.0014909 | -0.0014864 | -0.0015901 | -0.0013822 | 0.99815
6544 | 2224 | 2.9424 | 0 | 0 | 0 | 6.0322 | 1.8385 | 1.1172 | 15.6886 | 1.0792 | -0.0014864 | -0.0014819 | -0.0013822 | -0.0049178 | 2.126
6549 | 2229 | 2.9381 | 0 | 0 | 0 | 6.0161 | 1.8336 | 1.1122 | 15.6785 | 1.0778 | -0.0014819 | -0.0014775 | -0.0049178 | -0.0027862 | 2.6011
6554 | 2234 | 2.9338 | 0 | 0 | 0 | 6.0069 | 1.8308 | 1.1095 | 15.6742 | 1.0763 | -0.0014775 | -0.001473 | -0.0027862 | -0.0039 | 2.2673
6559 | 2239 | 2.9294 | 0 | 0 | 0 | 5.9941 | 1.8269 | 1.1056 | 15.6681 | 1.0748 | -0.001473 | -0.0014686 | -0.0039 | -0.0025099 | 2.1776
6564 | 2244 | 2.9251 | 0 | 0 | 0 | 5.9859 | 1.8244 | 1.103 | 15.6547 | 1.0733 | -0.0014686 | -0.0014642 | -0.0025099 | -0.0021941 | 1.6036
6569 | 2249 | 2.9209 | 0 | 0 | 0 | 5.9787 | 1.8222 | 1.1008 | 15.6159 | 1.0719 | -0.0014642 | -0.0014599 | -0.0021941 | -0.0021842 | 1.4973 | -0.011559 | -0.01129 | -0.020388 | -0.023886 | 1.9419
6574 | 2254 | 2.9166 | 0 | 0 | 0 | 5.9715 | 1.82 | 1.0987 | 15.6051 | 1.0704 | -0.0014599 | -0.0014555 | -0.0021842 | -0.0033 | 1.8823
6579 | 2259 | 2.9124 | 0 | 0 | 0 | 5.9607 | 1.8167 | 1.0954 | 15.604 | 1.069 | -0.0014555 | -0.0014512 | -0.0033 | -0.0024 | 1.96
6584 | 2264 | 2.9081 | 0 | 0 | 0 | 5.9528 | 1.8143 | 1.093 | 15.5864 | 1.0675 | -0.0014512 | -0.0014469 | -0.0024 | -0.0034079 | 2.0051
6589 | 2269 | 2.9039 | 0 | 0 | 0 | 5.9417 | 1.8109 | 1.0896 | 15.5872 | 1.0661 | -0.0014469 | -0.0014426 | -0.0034079 | -0.0020059 | 1.8722
6594 | 2274 | 2.8997 | 0 | 0 | 0 | 5.9351 | 1.8089 | 1.0876 | 15.5898 | 1.0646 | -0.0014426 | -0.0014384 | -0.0020059 | -0.001902 | 1.3563
6599 | 2279 | 2.8956 | 0 | 0 | 0 | 5.9288 | 1.807 | 1.0856 | 15.5898 | 1.0632 | -0.0014384 | -0.0014341 | -0.001902 | -0.0065941 | 2.9625
6604 | 2284 | 2.8914 | 0 | 0 | 0 | 5.9072 | 1.8004 | 1.0791 | 15.5942 | 1.0617 | -0.0014341 | -0.0014299 | -0.0065941 | 0.0014059 | 1.8033
6609 | 2289 | 2.8873 | 0 | 0 | 0 | 5.9118 | 1.8018 | 1.0805 | 15.582 | 1.0603 | -0.0014299 | -0.0014257 | 0.0014059 | -0.0014079 | 0.0035877 | -0.01129 | -0.011031 | -0.023886 | -0.024116 | 2.1514
6614 | 2294 | 2.8832 | 0 | 0 | 0 | 5.9072 | 1.8004 | 1.0791 | 15.5846 | 1.0589 | -0.0014257 | -0.0014215 | -0.0014079 | -0.004996 | 2.2529
6619 | 2299 | 2.8791 | 0 | 0 | 0 | 5.8908 | 1.7954 | 1.0741 | 15.5789 | 1.0575 | -0.0014215 | -0.0014174 | -0.004996 | -0.004002 | 3.1685
6624 | 2304 | 2.875 | 0 | 0 | 0 | 5.8777 | 1.7914 | 1.0701 | 15.585 | 1.0561 | -0.0014174 | -0.0014132 | -0.004002 | -0.002002 | 2.119
6629 | 2309 | 2.8709 | 0 | 0 | 0 | 5.8711 | 1.7894 | 1.0681 | 15.5833 | 1.0546 | -0.0014132 | -0.0014091 | -0.002002 | -0.0036901 | 2.0185
6634 | 2314 | 2.8669 | 0 | 0 | 0 | 5.859 | 1.7857 | 1.0644 | 15.5849 | 1.0532 | -0.0014091 | -0.001405 | -0.0036901 | -0.0021921 | 2.0887
6639 | 2319 | 2.8629 | 0 | 0 | 0 | 5.8518 | 1.7835 | 1.0622 | 15.5923 | 1.0518 | -0.001405 | -0.0014009 | -0.0021921 | -0.001502 | 1.3158
6644 | 2324 | 2.8589 | 0 | 0 | 0 | 5.8469 | 1.782 | 1.0607 | 15.5786 | 1.0504 | -0.0014009 | -0.0013969 | -0.001502 | -0.0040941 | 2.0028
6649 | 2329 | 2.8549 | 0 | 0 | 0 | 5.8334 | 1.7779 | 1.0566 | 15.5866 | 1.049 | -0.0013969 | -0.0013928 | -0.0040941 | -0.0031941 | 2.6116 | -0.011031 | -0.010782 | -0.024116 | -0.020296 | 2.0326
6654 | 2334 | 2.8509 | 0 | 0 | 0 | 5.823 | 1.7748 | 1.0534 | 15.5782 | 1.0476 | -0.0013928 | -0.0013888 | -0.0031941 | -0.001202 | 1.5783
6659 | 2339 | 2.8469 | 0 | 0 | 0 | 5.819 | 1.7735 | 1.0522 | 15.5878 | 1.0462 | -0.0013888 | -0.0013848 | -0.001202 | -0.003502 | 1.6984
6664 | 2344 | 2.843 | 0 | 0 | 0 | 5.8075 | 1.77 | 1.0487 | 15.5976 | 1.0449 | -0.0013848 | -0.0013808 | -0.003502 | -0.0059921 | 3.4355
6669 | 2349 | 2.8391 | 0 | 0 | 0 | 5.7879 | 1.7641 | 1.0427 | 15.5888 | 1.0435 | -0.0013808 | -0.0013768 | -0.0059921 | 0.00027631 | 2.0662
6674 | 2354 | 2.8352 | 0 | 0 | 0 | 5.7888 | 1.7643 | 1.043 | 15.6002 | 1.0421 | -0.0013768 | -0.0013729 | 0.00027631 | -0.00090197 | 0.22877
6679 | 2359 | 2.8313 | 0 | 0 | 0 | 5.7858 | 1.7634 | 1.0421 | 15.6063 | 1.0407 | -0.0013729 | -0.001369 | -0.00090197 | -0.005496 | 2.3383
6684 | 2364 | 2.8274 | 0 | 0 | 0 | 5.7678 | 1.7579 | 1.0366 | 15.5935 | 1.0394 | -0.001369 | -0.0013651 | -0.005496 | -0.004104 | 3.5099
6689 | 2369 | 2.8236 | 0 | 0 | 0 | 5.7543 | 1.7538 | 1.0325 | 15.5928 | 1.038 | -0.0013651 | -0.0013612 | -0.004104 | -0.001598 | 2.0889 | -0.010782 | -0.010541 | -0.020296 | -0.022788 | 2.0237
6694 | 2374 | 2.8197 | 0 | 0 | 0 | 5.7491 | 1.7522 | 1.0309 | 15.5908 | 1.0366 | -0.0013612 | -0.0013573 | -0.001598 | 0.0016039 | -0.0055383
6699 | 2379 | 2.8159 | 0 | 0 | 0 | 5.7543 | 1.7538 | 1.0325 | 15.5995 | 1.0353 | -0.0013573 | -0.0013534 | 0.0016039 | -0.0057862 | 1.5506
6704 | 2384 | 2.8121 | 0 | 0 | 0 | 5.7353 | 1.748 | 1.0267 | 15.5981 | 1.0339 | -0.0013534 | -0.0013496 | -0.0057862 | -0.0041099 | 3.6594
6709 | 2389 | 2.8083 | 0 | 0 | 0 | 5.7219 | 1.7439 | 1.0226 | 15.5952 | 1.0326 | -0.0013496 | -0.0013457 | -0.0041099 | -0.0050882 | 3.4136
6714 | 2394 | 2.8045 | 0 | 0 | 0 | 5.7052 | 1.7389 | 1.0175 | 15.5991 | 1.0312 | -0.0013457 | -0.0013419 | -0.0050882 | 0.0025901 | 0.92134
6719 | 2399 | 2.8008 | 0 | 0 | 0 | 5.7137 | 1.7414 | 1.0201 | 15.6022 | 1.0299 | -0.0013419 | -0.0013382 | 0.0025901 | -0.0074197 | 1.8126
6724 | 2404 | 2.797 | 0 | 0 | 0 | 5.6893 | 1.734 | 1.0127 | 15.6076 | 1.0285 | -0.0013382 | -0.0013344 | -0.0074197 | -0.00048815 | 2.9516
6729 | 2409 | 2.7933 | 0 | 0 | 0 | 5.6877 | 1.7335 | 1.0122 | 15.6042 | 1.0272 | -0.0013344 | -0.0013306 | -0.00048815 | -0.0036822 | 1.5683 | -0.010541 | -0.010309 | -0.022788 | -0.025562 | 2.3224
6734 | 2414 | 2.7896 | 0 | 0 | 0 | 5.6756 | 1.7299 | 1.0085 | 15.6069 | 1.0259 | -0.0013306 | -0.0013269 | -0.0036822 | -0.0026059 | 2.3651
6739 | 2419 | 2.7859 | 0 | 0 | 0 | 5.6671 | 1.7272 | 1.0059 | 15.6088 | 1.0246 | -0.0013269 | -0.0013232 | -0.0026059 | -0.0036941 | 2.3785
6744 | 2424 | 2.7822 | 0 | 0 | 0 | 5.655 | 1.7236 | 1.0022 | 15.594 | 1.0232 | -0.0013232 | -0.0013195 | -0.0036941 | -0.0010842 | 1.8054
6749 | 2429 | 2.7785 | 0 | 0 | 0 | 5.6514 | 1.7225 | 1.0011 | 15.6006 | 1.0219 | -0.0013195 | -0.0013158 | -0.0010842 | -0.0034099 | 1.7079
6754 | 2434 | 2.7749 | 0 | 0 | 0 | 5.6402 | 1.7191 | 0.99769 | 15.6057 | 1.0206 | -0.0013158 | -0.0013121 | -0.0034099 | -0.0031118 | 2.4814
6759 | 2439 | 2.7712 | 0 | 0 | 0 | 5.63 | 1.7159 | 0.99458 | 15.5939 | 1.0193 | -0.0013121 | -0.0013084 | -0.0031118 | -0.0033941 | 2.483
6764 | 2444 | 2.7676 | 0 | 0 | 0 | 5.6189 | 1.7126 | 0.99118 | 15.6094 | 1.018 | -0.0013084 | -0.0013048 | -0.0033941 | -0.0018059 | 1.9882
6769 | 2449 | 2.764 | 0 | 0 | 0 | 5.613 | 1.7107 | 0.98938 | 15.6066 | 1.0167 | -0.0013048 | -0.0013012 | -0.0018059 | -0.00058618 | 0.91663 | -0.010309 | -0.010086 | -0.025562 | -0.020402 | 2.2487
6774 | 2454 | 2.7604 | 0 | 0 | 0 | 5.611 | 1.7102 | 0.98879 | 15.603 | 1.0154 | -0.0013012 | -0.0012976 | -0.00058618 | -0.0040961 | 1.8055
6779 | 2459 | 2.7568 | 0 | 0 | 0 | 5.5976 | 1.7061 | 0.98469 | 15.6042 | 1.0141 | -0.0012976 | -0.001294 | -0.0040961 | -0.0043822 | 3.2718
6784 | 2464 | 2.7532 | 0 | 0 | 0 | 5.5832 | 1.7017 | 0.98031 | 15.6004 | 1.0128 | -0.001294 | -0.0012904 | -0.0043822 | -0.0010921 | 2.1147
6789 | 2469 | 2.7497 | 0 | 0 | 0 | 5.5796 | 1.7006 | 0.97922 | 15.5966 | 1.0115 | -0.0012904 | -0.0012868 | -0.0010921 | -0.0060882 | 2.7914
6794 | 2474 | 2.7462 | 0 | 0 | 0 | 5.5597 | 1.6945 | 0.97313 | 15.6036 | 1.0102 | -0.0012868 | -0.0012833 | -0.0060882 | -0.0034039 | 3.6903
6799 | 2479 | 2.7426 | 0 | 0 | 0 | 5.5485 | 1.6911 | 0.96973 | 15.6008 | 1.0089 | -0.0012833 | -0.0012798 | -0.0034039 | 0.0013901 | 0.78055
6804 | 2484 | 2.7391 | 0 | 0 | 0 | 5.553 | 1.6925 | 0.97112 | 15.6008 | 1.0076 | -0.0012798 | -0.0012763 | 0.0013901 | -0.0073039 | 2.323
6809 | 2489 | 2.7356 | 0 | 0 | 0 | 5.5291 | 1.6852 | 0.96381 | 15.589 | 1.0064 | -0.0012763 | -0.0012728 | -0.0073039 | -0.0013901 | 3.4044 | -0.010086 | -0.0098695 | -0.020402 | -0.0184 | 1.9428
6814 | 2494 | 2.7322 | 0 | 0 | 0 | 5.5245 | 1.6838 | 0.96242 | 15.5942 | 1.0051 | -0.0012728 | -0.0012693 | -0.0013901 | -0.0019921 | 1.3312
6819 | 2499 | 2.7287 | 0 | 0 | 0 | 5.518 | 1.6818 | 0.96043 | 15.5961 | 1.0038 | -0.0012693 | -0.0012658 | -0.0019921 | -0.002098 | 1.6135
6824 | 2504 | 2.7252 | 0 | 0 | 0 | 5.5111 | 1.6797 | 0.95833 | 15.5844 | 1.0026 | -0.0012658 | -0.0012624 | -0.002098 | -0.0016862 | 1.4964
6829 | 2509 | 2.7218 | 0 | 0 | 0 | 5.5056 | 1.678 | 0.95665 | 15.6049 | 1.0013 | -0.0012624 | -0.0012589 | -0.0016862 | -0.0036 | 2.0987
6834 | 2514 | 2.7184 | 0 | 0 | 0 | 5.4938 | 1.6744 | 0.95305 | 15.5894 | 1 | -0.0012589 | -0.0012555 | -0.0036 | -0.0052158 | 3.5078
6839 | 2519 | 2.715 | 0 | 0 | 0 | 5.4766 | 1.6692 | 0.94783 | 15.5832 | 0.99878 | -0.0012555 | -0.0012521 | -0.0052158 | -0.0035217 | 3.4825
6844 | 2524 | 2.7116 | 0 | 0 | 0 | 5.4651 | 1.6657 | 0.94431 | 15.588 | 0.99753 | -0.0012521 | -0.0012487 | -0.0035217 | -0.00089803 | 1.7645
6849 | 2529 | 2.7082 | 0 | 0 | 0 | 5.4621 | 1.6648 | 0.94341 | 15.592 | 0.99628 | -0.0012487 | -0.0012453 | -0.00089803 | -0.002 | 1.1632 | -0.0098695 | -0.0096607 | -0.0184 | -0.026449 | 2.3057
6854 | 2534 | 2.7048 | 0 | 0 | 0 | 5.4556 | 1.6628 | 0.94141 | 15.5946 | 0.99503 | -0.0012453 | -0.001242 | -0.002 | -0.0053 | 2.9385
6859 | 2539 | 2.7015 | 0 | 0 | 0 | 5.4382 | 1.6575 | 0.93611 | 15.595 | 0.99379 | -0.001242 | -0.0012386 | -0.0053 | 0.0009 | 1.767
6864 | 2544 | 2.6981 | 0 | 0 | 0 | 5.4411 | 1.6584 | 0.93701 | 15.5868 | 0.99255 | -0.0012386 | -0.0012353 | 0.0009 | -0.0059 | 2.0285
6869 | 2549 | 2.6948 | 0 | 0 | 0 | 5.4218 | 1.6525 | 0.93111 | 15.5906 | 0.99132 | -0.0012353 | -0.001232 | -0.0059 | -0.0017 | 3.0757
6874 | 2554 | 2.6915 | 0 | 0 | 0 | 5.4162 | 1.6508 | 0.92941 | 15.585 | 0.99009 | -0.001232 | -0.0012287 | -0.0017 | -0.0021901 | 1.5815
6879 | 2559 | 2.6882 | 0 | 0 | 0 | 5.409 | 1.6486 | 0.92722 | 15.5873 | 0.98886 | -0.0012287 | -0.0012254 | -0.0021901 | -0.00099802 | 1.2978
6884 | 2564 | 2.6849 | 0 | 0 | 0 | 5.4058 | 1.6476 | 0.92622 | 15.5912 | 0.98763 | -0.0012254 | -0.0012221 | -0.00099802 | -0.0012119 | 0.90314
6889 | 2569 | 2.6816 | 0 | 0 | 0 | 5.4018 | 1.6464 | 0.92501 | 15.5868 | 0.98641 | -0.0012221 | -0.0012189 | -0.0012119 | -0.0045059 | 2.346 | -0.0096607 | -0.009459 | -0.026449 | -0.017649 | 2.2972
6894 | 2574 | 2.6783 | 0 | 0 | 0 | 5.387 | 1.6419 | 0.92051 | 15.5852 | 0.98519 | -0.0012189 | -0.0012156 | -0.0045059 | -0.0044901 | 3.6953
6899 | 2579 | 2.6751 | 0 | 0 | 0 | 5.3723 | 1.6374 | 0.91602 | 15.598 | 0.98397 | -0.0012156 | -0.0012124 | -0.0044901 | -0.0041881 | 3.5739
6904 | 2584 | 2.6718 | 0 | 0 | 0 | 5.3585 | 1.6332 | 0.91183 | 15.5961 | 0.98276 | -0.0012124 | -0.0012092 | -0.0041881 | -0.0031862 | 3.0442
6909 | 2589 | 2.6686 | 0 | 0 | 0 | 5.3481 | 1.63 | 0.90864 | 15.6034 | 0.98155 | -0.0012092 | -0.001206 | -0.0031862 | -0.00099013 | 1.7268
6914 | 2594 | 2.6654 | 0 | 0 | 0 | 5.3448 | 1.629 | 0.90765 | 15.608 | 0.98035 | -0.001206 | -0.0012028 | -0.00099013 | -0.00078815 | 0.73805
6919 | 2599 | 2.6622 | 0 | 0 | 0 | 5.3422 | 1.6282 | 0.90686 | 15.5988 | 0.97914 | -0.0012028 | -0.0011996 | -0.00078815 | -0.0065961 | 3.0802
6924 | 2604 | 2.659 | 0 | 0 | 0 | 5.3206 | 1.6216 | 0.90027 | 15.5844 | 0.97794 | -0.0011996 | -0.0011964 | -0.0065961 | -0.0017039 | 3.4587
6929 | 2609 | 2.6558 | 0 | 0 | 0 | 5.315 | 1.6199 | 0.89856 | 15.5833 | 0.97675 | -0.0011964 | -0.0011933 | -0.0017039 | -0.00039013 | 0.87485 | -0.009459 | -0.0092639 | -0.017649 | -0.021674 | 2.1052
6934 | 2614 | 2.6526 | 0 | 0 | 0 | 5.3137 | 1.6195 | 0.89817 | 15.5948 | 0.97556 | -0.0011933 | -0.0011901 | -0.00039013 | -0.0042 | 1.9301
6939 | 2619 | 2.6495 | 0 | 0 | 0 | 5.2999 | 1.6153 | 0.89397 | 15.5803 | 0.97437 | -0.0011901 | -0.001187 | -0.0042 | -0.00018618 | 1.8407
6944 | 2624 | 2.6463 | 0 | 0 | 0 | 5.2993 | 1.6152 | 0.89379 | 15.5822 | 0.97318 | -0.001187 | -0.0011839 | -0.00018618 | -0.0035803 | 1.5924
6949 | 2629 | 2.6432 | 0 | 0 | 0 | 5.2876 | 1.6116 | 0.89021 | 15.5799 | 0.97199 | -0.0011839 | -0.0011808 | -0.0035803 | -0.0012783 | 2.0521
6954 | 2634 | 2.6401 | 0 | 0 | 0 | 5.2834 | 1.6103 | 0.88893 | 15.5781 | 0.97081 | -0.0011808 | -0.0011777 | -0.0012783 | -0.004798 | 2.5803
6959 | 2639 | 2.637 | 0 | 0 | 0 | 5.2676 | 1.6055 | 0.88413 | 15.5878 | 0.96964 | -0.0011777 | -0.0011746 | -0.004798 | -0.0035059 | 3.5287
6964 | 2644 | 2.6339 | 0 | 0 | 0 | 5.2561 | 1.602 | 0.88062 | 15.5761 | 0.96846 | -0.0011746 | -0.0011716 | -0.0035059 | 0.00029013 | 1.3664
6969 | 2649 | 2.6308 | 0 | 0 | 0 | 5.2571 | 1.6023 | 0.88091 | 15.5818 | 0.96729 | -0.0011716 | -0.0011685 | 0.00029013 | -0.0013 | 0.43332 | -0.0092639 | -0.0090751 | -0.021674 | -0.016472 | 2.0747
6974 | 2654 | 2.6277 | 0 | 0 | 0 | 5.2528 | 1.601 | 0.87961 | 15.5902 | 0.96612 | -0.0011685 | -0.0011655 | -0.0013 | -0.005904 | 3.0917
6979 | 2659 | 2.6247 | 0 | 0 | 0 | 5.2335 | 1.5951 | 0.87371 | 15.5742 | 0.96496 | -0.0011655 | -0.0011625 | -0.005904 | -0.0012 | 3.0464
6984 | 2664 | 2.6216 | 0 | 0 | 0 | 5.2295 | 1.5939 | 0.87251 | 15.5844 | 0.96379 | -0.0011625 | -0.0011595 | -0.0012 | -0.0028 | 1.7245
6989 | 2669 | 2.6186 | 0 | 0 | 0 | 5.2203 | 1.5911 | 0.86971 | 15.5894 | 0.96263 | -0.0011595 | -0.0011565 | -0.0028 | -0.0020039 | 2.0734
6994 | 2674 | 2.6156 | 0 | 0 | 0 | 5.2138 | 1.5891 | 0.86771 | 15.5877 | 0.96148 | -0.0011565 | -0.0011535 | -0.0020039 | -0.0016862 | 1.5972
6999 | 2679 | 2.6125 | 0 | 0 | 0 | 5.2082 | 1.5874 | 0.86602 | 15.586 | 0.96032 | -0.0011535 | -0.0011505 | -0.0016862 | 0.00081185 | 0.3767
7004 | 2684 | 2.6095 | 0 | 0 | 0 | 5.2109 | 1.5882 | 0.86683 | 15.5887 | 0.95917 | -0.0011505 | -0.0011475 | 0.00081185 | -0.0075921 | 2.9599
7009 | 2689 | 2.6065 | 0 | 0 | 0 | 5.186 | 1.5806 | 0.85924 | 15.5887 | 0.95803 | -0.0011475 | -0.0011446 | -0.0075921 | 0.00020593 | 3.2137 | -0.0090751 | -0.94895 | -0.016472 | -0.84277 | 1.8063
7014 | 2694 | 2.6036 | 0 | 0 | 0 | 5.1867 | 1.5808 | 0.85945 | 15.5902 | 0.95688 | -0.0011446 | -0.0011417 | 0.00020593 | -0.003904 | 1.6221
7019 | 2699 | 2.6006 | 0 | 0 | 0 | 5.1738 | 1.5769 | 0.85554 | 15.5908 | 0.95574 | -0.0011417 | -0.0011387 | -0.003904 | -0.00039803 | 1.8826
7024 | 2704 | 2.5976 | 0 | 0 | 0 | 5.1725 | 1.5765 | 0.85514 | 15.5957 | 0.9546 | -0.0011387 | -0.0011358 | -0.00039803 | -0.0030921 | 1.5375
7029 | 2709 | 2.5947 | 0 | 0 | 0 | 5.1624 | 1.5734 | 0.85205 | 15.5973 | 0.95346 | -0.0011358 | -0.0011329 | -0.0030921 | -0.0039882 | 3.1218
7034 | 2714 | 2.5917 | 0 | 0 | 0 | 5.1493 | 1.5694 | 0.84806 | 15.5932 | 0.95233 | -0.0011329 | -0.00113 | -0.0039882 | -0.0011178 | 2.2531
7039 | 2719 | 2.5888 | 0 | 0 | 0 | 5.1456 | 1.5683 | 0.84695 | 15.5932 | 0.9512 | -0.00113 | -0.0011271 | -0.0011178 | -0.0026119 | 1.654
7044 | 2724 | 2.5859 | 0 | 0 | 0 | 5.1371 | 1.5657 | 0.84433 | 15.5937 | 0.95007 | -0.0011271 | -0.0011243 | -0.0026119 | -0.0015664 | 1.8547
7049 | 2729 | 2.583 | 0 | 0 | 0 | 5.1319 | 1.5641 | 0.84277 | 15.5913 | 0.94895 | -0.0011243 | -0.0011214 | -0.0015664 | -0.0014862 | 1.3592 | -0.94895 | 0 | -0.84277 | 0 | #DIV/0!
7054 | 2734 | 2.5801 | 0 | 0 | 0 | 5.1271 | 1.5627 | 0.84128 | 15.5992 | 0.94783 | -0.0011214 | -0.0011186 | -0.0014862 | -0.0019158 | 1.5192
7059 | 2739 | 2.5772 | 0 | 0 | 0 | 5.1208 | 1.5607 | 0.83937 | 15.6037 | 0.94671 | -0.0011186 | -0.0011158 | -0.0019158 | -0.002804 | 2.1134
7064 | 2744 | 2.5743 | 0 | 0 | 0 | 5.1116 | 1.5579 | 0.83656 | 15.609 | 0.94559 | -0.0011158 | -0.94559 | -0.002804 | -0.83656 | 2.5111

## Hydraulic Paramaters
Aquifer Hydraulic Paramaters | [12 empty] | Well Hydraulic Paramaters
| Theis Curve-Matching Method |  |  |  | Cooper-Jacob Straight Line Method |  |  |  | Theis Recovery Method |  |  |  |  | Long Term Yield (100 day method)
|  | Equations |  |  |  | Equations |  |  |  | Equations |  |  |  |  | Equations
| T = ( Q * W (u) ) / ( 4 * pi * s ) |  |  |  | T = ( 2.3 * Q ) / ( 4 * pi * slope ) |  |  |  | T = ( 2.3 * Q ) / ( 4 * pi * slope ) |  |  |  |  | Q100 = SAD*SC = 0.7*Available DD*Q/100 Day DD
Available DD = SWL-Water bearing fracture
|  | Variables |  |  |  | Variables |  |  |  | Variables |  |  |  |  | Variables
| Note: Taken from radial flow time segment |  |  |  | Note: Taken from radial flow time segment |  |  |  | Note: Taken from radial flow time segment |  |  |  |  | Q (Discharge Rate) |  | 39.02 | m3/day
[14 empty] | 100 Day DD |  | 21 | m
| Match Point |  |  |  | Slope is for 1 log10 cycle of time |  |  |  | Slope is for 1 log10 cycle of time |  |  |  |  | Well Depth |  | 27.62 | m
| s (Drawdown) |  | 10 | m | Q (Discharge Rate) |  | 38.02 | m3/day | [5 empty] | SWL |  | 0.721 | m
| t (time) |  | 75 | min | slope (ds/dlog(t)) |  | 3.7 | m | Q (Discharge Rate) |  | 38.02 | m3/day |  | Water bearing fracture |  | 24.4 | m
| W(u) |  | 5 |  | to (Intercept Time) |  | N/A |  | slope (ds/dlog(t/t')) |  | 4.1 | m
| 1/u |  | 125 |  | r (Radius) |  | N/A |  | to (Intercept Time) |  | N/A
[9 empty] | r (Radius) |  | N/A
| Q ((Discharge Rate) |  | 38.02 | m3/day
| r (Radius) |  | N/A | m
| T (Transmissivity) |  | 1.5128 | m2/day | T (Transmissivity) |  | 1.8901 | m2/day | T (Transmissivity) |  | 1.6968 | m2/day |  | Q100 |  | 30.7985 | m3/day
Match Point
100 Day Drawdown = 21 m
100 Days
ds/d(log(t/t')) = 4.1