## Pumped Well Info
WELL, TEST, AQUIFER INFORMATION FOR PUMPING WELL
Well Information |  | Test Information |  | Aquifer Information
Well Name: | Noowick Production | Date of start of test (yyyy-mm-dd): | 2019-10-29 | Aquifer Number: | 208
Well ID Plate Number: | 53503 | Type of test (step test, constant rate test): | constant rate test | Aquifer Lithology | West Coast Crystalline Complex
Well Tag Number: | 119110 | SWL at start of test (m): | 29.69 | Aquifer Type: | Fractured Crystalline Bedrock
Well Location : | Mill Bay, BC | Reference datum for water level measurements (top of production casing): |  | Depth to upper-most water bearing fracture (m) | 131
UTM Zone (easting, northing): |  | Datalogger water level measurements?: | yes
Well Casing Inside Diameter (mm): | 250 | Was a step-drawdown test performed before the constant rate test? | No

## Pumped Well Data
Pumped Well Data
WPID: | 53503 | SWL (m): | 30.91 |  | Average Pumping Rate (m3/day): |  |  | 362.9
Derivative is very noisy due to the excess of measuments. Derivative will be easier to interpret with a greater L-spacing inverval (3 was chosen)
Time since pumping started, t (min) | Time since pumping stopped, t' (min) | t/t' | Pumping rate, Q (USgpm) | Pumping rate, Q (L/s) | Pumping Rate, Q (m3/day) | Water Level (ft) | Water Level (m) | Drawdown or Residual Drawdown (m) | Extended Drawdown (m) | ln(t) | Dt1 | Dt2 | Ds1 | Ds2 | ds/dt | Dt1 | Dt2 | Ds1 | Ds2 | ds/dt (L-Spacing = 3) | d2s/dt2
0 | - | - | 66.57 | 4.2 | 362.9 | 101.6792 | 30.9105 | 0 | 0 | #NUM! | #NUM! | #NUM! | #VALUE! | 4.107 | #VALUE!
30 | - | - | 66.57 | 4.2 | 362.9 | 115.189 | 35.0175 | 4.107 | 4.107 | 3.4012 | #NUM! | 0.69315 | 4.107 | 0.9413 | #NUM!
60 | - | - | 66.57 | 4.2 | 362.9 | 118.2854 | 35.9588 | 5.0483 | 5.0483 | 4.0943 | 0.69315 | 0.40547 | 0.9413 | 0.5766 | 1.3984 | 0.91629 | 0.47 | 1.3623 | 0.9529 | 1.8441 | 0.39425
90 | - | - | 66.57 | 4.2 | 362.9 | 120.1821 | 36.5354 | 5.6249 | 5.6249 | 4.4998 | 0.40547 | 0.28768 | 0.5766 | 0.4517 | 1.5087
120 | - | - | 66.57 | 4.2 | 362.9 | 121.668 | 36.9871 | 6.0766 | 6.0766 | 4.7875 | 0.28768 | 0.22314 | 0.4517 | 0.334 | 1.5288
150 | - | - | 66.57 | 4.2 | 362.9 | 122.7666 | 37.3211 | 6.4106 | 6.4106 | 5.0106 | 0.22314 | 0.18232 | 0.334 | 0.3387 | 1.6954 | 0.47 | 0.31845 | 0.9529 | 0.7407 | 2.2054 | 0.56314
180 | - | - | 66.57 | 4.2 | 362.9 | 123.8808 | 37.6598 | 6.7493 | 6.7493 | 5.193 | 0.18232 | 0.15415 | 0.3387 | 0.289 | 1.867
210 | - | - | 66.57 | 4.2 | 362.9 | 124.8314 | 37.9488 | 7.0383 | 7.0383 | 5.3471 | 0.15415 | 0.13353 | 0.289 | 0.3252 | 2.1752
240 | - | - | 66.57 | 4.2 | 362.9 | 125.9012 | 38.274 | 7.3635 | 7.3635 | 5.4806 | 0.13353 | 0.11778 | 0.3252 | 0.2788 | 2.3991 | 0.31845 | 0.24116 | 0.7407 | 0.622 | 2.47 | 1.1261
270 | - | - | 66.57 | 4.2 | 362.9 | 126.8183 | 38.5528 | 7.6423 | 7.6423 | 5.5984 | 0.11778 | 0.10536 | 0.2788 | 0.2363 | 2.3015
300 | - | - | 66.57 | 4.2 | 362.9 | 127.5956 | 38.7891 | 7.8786 | 7.8786 | 5.7038 | 0.10536 | 0.09531 | 0.2363 | 0.2256 | 2.308
330 | - | - | 66.57 | 4.2 | 362.9 | 128.3377 | 39.0147 | 8.1042 | 8.1042 | 5.7991 | 0.09531 | 0.087011 | 0.2256 | 0.2079 | 2.3787 | 0.24116 | 0.19416 | 0.622 | 0.5882 | 2.8287 | 1.3363
360 | - | - | 66.57 | 4.2 | 362.9 | 129.0216 | 39.2226 | 8.3121 | 8.3121 | 5.8861 | 0.087011 | 0.080043 | 0.2079 | 0.2192 | 2.5712
390 | - | - | 66.57 | 4.2 | 362.9 | 129.7426 | 39.4418 | 8.5313 | 8.5313 | 5.9661 | 0.080043 | 0.074108 | 0.2192 | 0.1949 | 2.6822
420 | - | - | 66.57 | 4.2 | 362.9 | 130.3837 | 39.6367 | 8.7262 | 8.7262 | 6.0403 | 0.074108 | 0.068993 | 0.1949 | 0.2348 | 3.0304 | 0.19416 | 0.16252 | 0.5882 | 0.5286 | 3.1509 | 2.4734
450 | - | - | 66.57 | 4.2 | 362.9 | 131.1561 | 39.8715 | 8.961 | 8.961 | 6.1092 | 0.068993 | 0.064539 | 0.2348 | 0.1417 | 2.7793
480 | - | - | 66.57 | 4.2 | 362.9 | 131.6222 | 40.0132 | 9.1027 | 9.1027 | 6.1738 | 0.064539 | 0.060625 | 0.1417 | 0.2117 | 2.8641
510 | - | - | 66.57 | 4.2 | 362.9 | 132.3186 | 40.2249 | 9.3144 | 9.3144 | 6.2344 | 0.060625 | 0.057158 | 0.2117 | 0.1779 | 3.2966 | 0.16252 | 0.13976 | 0.5286 | 0.553 | 3.6311 | 7.6444
540 | - | - | 66.57 | 4.2 | 362.9 | 132.9038 | 40.4028 | 9.4923 | 9.4923 | 6.2916 | 0.057158 | 0.054067 | 0.1779 | 0.1463 | 2.9035
570 | - | - | 66.57 | 4.2 | 362.9 | 133.385 | 40.5491 | 9.6386 | 9.6386 | 6.3456 | 0.054067 | 0.051293 | 0.1463 | 0.2044 | 3.3622
600 | - | - | 66.57 | 4.2 | 362.9 | 134.0574 | 40.7535 | 9.843 | 9.843 | 6.3969 | 0.051293 | 0.04879 | 0.2044 | 0.1962 | 4.0036 | 0.13976 | 0.1226 | 0.553 | 0.6961 | 4.8735 | 7.071
630 | - | - | 66.57 | 4.2 | 362.9 | 134.7028 | 40.9497 | 10.0392 | 10.0392 | 6.4457 | 0.04879 | 0.04652 | 0.1962 | 0.1819 | 3.9644
660 | - | - | 66.57 | 4.2 | 362.9 | 135.3012 | 41.1316 | 10.2211 | 10.2211 | 6.4922 | 0.04652 | 0.044452 | 0.1819 | 0.1749 | 3.9227
690 | - | - | 66.57 | 4.2 | 362.9 | 135.8765 | 41.3065 | 10.396 | 10.396 | 6.5367 | 0.044452 | 0.04256 | 0.1749 | 0.2535 | 4.9675 | 0.1226 | 0.1092 | 0.6961 | 0.658 | 5.8618 | -4.3873
720 | - | - | 66.57 | 4.2 | 362.9 | 136.7104 | 41.56 | 10.6495 | 10.6495 | 6.5793 | 0.04256 | 0.040822 | 0.2535 | 0.1503 | 4.7954
750 | - | - | 66.57 | 4.2 | 362.9 | 137.2048 | 41.7103 | 10.7998 | 10.7998 | 6.6201 | 0.040822 | 0.039221 | 0.1503 | 0.2923 | 5.605
780 | - | - | 66.57 | 4.2 | 362.9 | 138.1663 | 42.0026 | 11.0921 | 11.0921 | 6.6593 | 0.039221 | 0.03774 | 0.2923 | 0.2089 | 6.4755 | 0.1092 | 0.09844 | 0.658 | 0.4618 | 5.3239 | 5.8312
810 | - | - | 66.57 | 4.2 | 362.9 | 138.8535 | 42.2115 | 11.301 | 11.301 | 6.697 | 0.03774 | 0.036368 | 0.2089 | 0.2413 | 6.0953
840 | - | - | 66.57 | 4.2 | 362.9 | 139.6472 | 42.4528 | 11.5423 | 11.5423 | 6.7334 | 0.036368 | 0.035091 | 0.2413 | 0.2078 | 6.272
870 | - | - | 66.57 | 4.2 | 362.9 | 140.3308 | 42.6606 | 11.7501 | 11.7501 | 6.7685 | 0.035091 | 0.033902 | 0.2078 | 0.1848 | 5.6823 | 0.09844 | 0.089612 | 0.4618 | 0.6377 | 5.9606 | 3.6344
900 | - | - | 66.57 | 4.2 | 362.9 | 140.9387 | 42.8454 | 11.9349 | 11.9349 | 6.8024 | 0.033902 | 0.03279 | 0.1848 | 0.1122 | 4.4195
930 | - | - | 66.57 | 4.2 | 362.9 | 141.3077 | 42.9576 | 12.0471 | 12.0471 | 6.8352 | 0.03279 | 0.031749 | 0.1122 | 0.1648 | 4.3205
960 | - | - | 66.57 | 4.2 | 362.9 | 141.8498 | 43.1224 | 12.2119 | 12.2119 | 6.8669 | 0.031749 | 0.030772 | 0.1648 | 0.197 | 5.8058 | 0.089612 | 0.082238 | 0.6377 | 0.4594 | 6.3184 | -9.5806
990 | - | - | 66.57 | 4.2 | 362.9 | 142.4979 | 43.3194 | 12.4089 | 12.4089 | 6.8977 | 0.030772 | 0.029853 | 0.197 | 0.2176 | 6.8522
1020 | - | - | 66.57 | 4.2 | 362.9 | 143.2137 | 43.537 | 12.6265 | 12.6265 | 6.9276 | 0.029853 | 0.028988 | 0.2176 | 0.2231 | 7.4957
1050 | - | - | 66.57 | 4.2 | 362.9 | 143.9475 | 43.7601 | 12.8496 | 12.8496 | 6.9565 | 0.028988 | 0.028171 | 0.2231 | 0.1049 | 5.6817 | 0.082238 | 0.075986 | 0.4594 | 0.406 | 5.4599 | -4.9555
1080 | - | - | 66.57 | 4.2 | 362.9 | 144.2926 | 43.865 | 12.9545 | 12.9545 | 6.9847 | 0.028171 | 0.027399 | 0.1049 | 0.1958 | 5.4587
1110 | - | - | 66.57 | 4.2 | 362.9 | 144.9367 | 44.0608 | 13.1503 | 13.1503 | 7.0121 | 0.027399 | 0.026668 | 0.1958 | 0.1587 | 6.5405
1140 | - | - | 66.57 | 4.2 | 362.9 | 145.4587 | 44.2195 | 13.309 | 13.309 | 7.0388 | 0.026668 | 0.025975 | 0.1587 | 0.1185 | 5.2473 | 0.075986 | 0.070618 | 0.406 | 0.3377 | 5.0523 | 2.2605
1170 | - | - | 66.57 | 4.2 | 362.9 | 145.8485 | 44.338 | 13.4275 | 13.4275 | 7.0648 | 0.025975 | 0.025318 | 0.1185 | 0.1356 | 4.964
1200 | - | - | 66.57 | 4.2 | 362.9 | 146.2946 | 44.4736 | 13.5631 | 13.5631 | 7.0901 | 0.025318 | 0.024693 | 0.1356 | 0.1519 | 5.7587
1230 | - | - | 66.57 | 4.2 | 362.9 | 146.7942 | 44.6255 | 13.715 | 13.715 | 7.1148 | 0.024693 | 0.024098 | 0.1519 | 0.1078 | 5.3023 | 0.070618 | 0.065958 | 0.3377 | 0.3718 | 5.2241 | 6.8743
1260 | - | - | 66.57 | 4.2 | 362.9 | 147.1488 | 44.7333 | 13.8228 | 13.8228 | 7.1389 | 0.024098 | 0.02353 | 0.1078 | 0.1344 | 5.1
1290 | - | - | 66.57 | 4.2 | 362.9 | 147.591 | 44.8677 | 13.9572 | 13.9572 | 7.1624 | 0.02353 | 0.02299 | 0.1344 | 0.0955 | 4.9238
1320 | - | - | 66.57 | 4.2 | 362.9 | 147.9051 | 44.9632 | 14.0527 | 14.0527 | 7.1854 | 0.02299 | 0.022473 | 0.0955 | 0.1022 | 4.3531 | 0.065958 | -4.0325 | 0.3718 | -5.1222 | 5.7095 | -66.0416
1350 | - | - | 66.57 | 4.2 | 362.9 | 148.2413 | 45.0654 | 14.1549 | 14.1549 | 7.2079 | 0.022473 | 0.021979 | 0.1022 | 0.1753 | 6.2808
1380 | - | - | 66.57 | 4.2 | 362.9 | 148.8179 | 45.2407 | 14.3302 | 14.3302 | 7.2298 | 0.021979 | 0.021506 | 0.1753 | 0.0943 | 6.1608
1410 | - | - | 66.57 | 4.2 | 362.9 | 149.1281 | 45.335 | 14.4245 | 14.4245 | 7.2513 | 0.021506 | 0.021053 | 0.0943 | -0.2401 | -3.5938 | -4.0325 | -0.85802 | -5.1222 | -1.1766 | 1.3536 | -0.051886
1440 | - | - | 66.57 | 4.2 | 362.9 | 148.3383 | 45.0949 | 14.1844 | 14.1844 | 7.2724 | 0.021053 | #VALUE! | -0.2401 | -4.1363 | #VALUE!
1470 | 30 | 49 | 0 | 0 | 0 | 134.7321 | 40.9586 | 10.0481 | 14.1551 | ln(t/t') | D(t/t')1 | D(t/t')2 | Ds1 | Ds2 | ds/d(t/t') | D(t/t')1 | D(t/t')2 | Ds1 | Ds2 | ds/d(t/t') (L-Spacing = 3) | d2s/d(t/t')2
1500 | 60 | 25 | 0 | 0 | 0 | 132.2788 | 40.2128 | 9.3023 | 14.3506 | 3.2189 | #VALUE! | -0.38566 | -0.7458 | -0.499 | #VALUE! | -0.85802 | -0.41494 | -1.1766 | -0.6869 | 1.5628 | -0.28342
1530 | 90 | 17 | 0 | 0 | 0 | 130.6374 | 39.7138 | 8.8033 | 14.4282 | 2.8332 | -0.38566 | -0.26826 | -0.499 | -0.3735 | 1.3519
1560 | 120 | 13 | 0 | 0 | 0 | 129.4087 | 39.3403 | 8.4298 | 14.5064 | 2.5649 | -0.26826 | -0.2041 | -0.3735 | -0.3041 | 1.4478
1590 | 150 | 10.6 | 0 | 0 | 0 | 128.4084 | 39.0362 | 8.1257 | 14.5363 | 2.3609 | -0.2041 | -0.16363 | -0.3041 | -0.2616 | 1.5503 | -0.41494 | -0.26627 | -0.6869 | -0.5066 | 1.806 | -0.5089
1620 | 180 | 9 | 0 | 0 | 0 | 127.5479 | 38.7746 | 7.8641 | 14.6134 | 2.1972 | -0.16363 | -0.1358 | -0.2616 | -0.2265 | 1.6365
1650 | 210 | 7.8571 | 0 | 0 | 0 | 126.8028 | 38.5481 | 7.6376 | 14.6759 | 2.0614 | -0.1358 | -0.11551 | -0.2265 | -0.1988 | 1.6966
1680 | 240 | 7 | 0 | 0 | 0 | 126.1489 | 38.3493 | 7.4388 | 14.8023 | 1.9459 | -0.11551 | -0.10008 | -0.1988 | -0.182 | 1.7732 | -0.26627 | -0.19157 | -0.5066 | -0.4022 | 2.0171 | -0.85745
1710 | 270 | 6.3333 | 0 | 0 | 0 | 125.5502 | 38.1673 | 7.2568 | 14.8991 | 1.8458 | -0.10008 | -0.087969 | -0.182 | -0.1693 | 1.8749
1740 | 300 | 5.8 | 0 | 0 | 0 | 124.9933 | 37.998 | 7.0875 | 14.9661 | 1.7579 | -0.087969 | -0.078216 | -0.1693 | -0.1553 | 1.9568
1770 | 330 | 5.3636 | 0 | 0 | 0 | 124.4824 | 37.8427 | 6.9322 | 15.0364 | 1.6796 | -0.078216 | -0.070204 | -0.1553 | -0.1414 | 2.0006 | -0.19157 | -0.1469 | -0.4022 | -0.3463 | 2.2454 | -1.1513
1800 | 360 | 5 | 0 | 0 | 0 | 124.0173 | 37.7013 | 6.7908 | 15.1029 | 1.6094 | -0.070204 | -0.063513 | -0.1414 | -0.1319 | 2.047
1830 | 390 | 4.6923 | 0 | 0 | 0 | 123.5834 | 37.5694 | 6.6589 | 15.1902 | 1.5459 | -0.063513 | -0.057847 | -0.1319 | -0.1289 | 2.156
1860 | 420 | 4.4286 | 0 | 0 | 0 | 123.1594 | 37.4405 | 6.53 | 15.2562 | 1.4881 | -0.057847 | -0.052993 | -0.1289 | -0.1174 | 2.2216 | -0.1469 | -0.1174 | -0.3463 | -0.2997 | 2.466 | -1.4735
1890 | 450 | 4.2 | 0 | 0 | 0 | 122.7732 | 37.3231 | 6.4126 | 15.3736 | 1.4351 | -0.052993 | -0.04879 | -0.1174 | -0.1169 | 2.3094
1920 | 480 | 4 | 0 | 0 | 0 | 122.3887 | 37.2062 | 6.2957 | 15.3984 | 1.3863 | -0.04879 | -0.04512 | -0.1169 | -0.112 | 2.4408
1950 | 510 | 3.8235 | 0 | 0 | 0 | 122.0203 | 37.0942 | 6.1837 | 15.4981 | 1.3412 | -0.04512 | -0.041891 | -0.112 | -0.1015 | 2.4515 | -0.1174 | -0.09659 | -0.2997 | -0.2694 | 2.6825 | -1.7845
1980 | 540 | 3.6667 | 0 | 0 | 0 | 121.6864 | 36.9927 | 6.0822 | 15.5745 | 1.2993 | -0.041891 | -0.039029 | -0.1015 | -0.1022 | 2.5242
2010 | 570 | 3.5263 | 0 | 0 | 0 | 121.3502 | 36.8905 | 5.98 | 15.6186 | 1.2603 | -0.039029 | -0.036478 | -0.1022 | -0.096 | 2.6253
2040 | 600 | 3.4 | 0 | 0 | 0 | 121.0344 | 36.7945 | 5.884 | 15.727 | 1.2238 | -0.036478 | -0.034191 | -0.096 | -0.0949 | 2.706 | -0.09659 | -0.081217 | -0.2694 | -0.2419 | 2.892 | -1.9495
2070 | 630 | 3.2857 | 0 | 0 | 0 | 120.7222 | 36.6996 | 5.7891 | 15.8283 | 1.1896 | -0.034191 | -0.032131 | -0.0949 | -0.0869 | 2.7389
2100 | 660 | 3.1818 | 0 | 0 | 0 | 120.4364 | 36.6127 | 5.7022 | 15.9233 | 1.1575 | -0.032131 | -0.030267 | -0.0869 | -0.0876 | 2.8022
2130 | 690 | 3.087 | 0 | 0 | 0 | 120.1482 | 36.5251 | 5.6146 | 16.0106 | 1.1272 | -0.030267 | -0.028573 | -0.0876 | -0.0825 | 2.8907 | -0.081217 | -0.069459 | -0.2419 | -0.22 | 3.0803 | -1.649
2160 | 720 | 3 | 0 | 0 | 0 | 119.8768 | 36.4426 | 5.5321 | 16.1816 | 1.0986 | -0.028573 | -0.027029 | -0.0825 | -0.0812 | 2.9474
2190 | 750 | 2.92 | 0 | 0 | 0 | 119.6097 | 36.3614 | 5.4509 | 16.2507 | 1.0716 | -0.027029 | -0.025615 | -0.0812 | -0.0782 | 3.0292
2220 | 780 | 2.8462 | 0 | 0 | 0 | 119.3525 | 36.2832 | 5.3727 | 16.4648 | 1.046 | -0.025615 | -0.024317 | -0.0782 | -0.0754 | 3.0774 | -0.069459 | -0.060219 | -0.22 | -0.196 | 3.2142 | -1.7256
2250 | 810 | 2.7778 | 0 | 0 | 0 | 119.1045 | 36.2078 | 5.2973 | 16.5983 | 1.0217 | -0.024317 | -0.023122 | -0.0754 | -0.0748 | 3.1695
2280 | 840 | 2.7143 | 0 | 0 | 0 | 118.8584 | 36.133 | 5.2225 | 16.7648 | 0.99853 | -0.023122 | -0.022019 | -0.0748 | -0.0698 | 3.2017
2310 | 870 | 2.6552 | 0 | 0 | 0 | 118.6288 | 36.0632 | 5.1527 | 16.9028 | 0.97651 | -0.022019 | -0.020998 | -0.0698 | -0.0683 | 3.2123 | -0.060219 | -0.052798 | -0.196 | -0.1797 | 3.334 | 11.1653
2340 | 900 | 2.6 | 0 | 0 | 0 | 118.4041 | 35.9949 | 5.0844 | 17.0193 | 0.95551 | -0.020998 | -0.020051 | -0.0683 | -0.0623 | 3.1782
2370 | 930 | 2.5484 | 0 | 0 | 0 | 118.1992 | 35.9326 | 5.0221 | 17.0692 | 0.93546 | -0.020051 | -0.01917 | -0.0623 | -0.0654 | 3.2628
2400 | 960 | 2.5 | 0 | 0 | 0 | 117.9841 | 35.8672 | 4.9567 | 17.1686 | 0.91629 | -0.01917 | -0.018349 | -0.0654 | -0.0613 | 3.3754 | -0.052798 | -0.046731 | -0.1797 | -0.0937 | 2.6617 | -4.5339
2430 | 990 | 2.4545 | 0 | 0 | 0 | 117.7824 | 35.8059 | 4.8954 | 17.3043 | 0.89794 | -0.018349 | -0.017583 | -0.0613 | -0.0629 | 3.4616
2460 | 1020 | 2.4118 | 0 | 0 | 0 | 117.5755 | 35.743 | 4.8325 | 17.459 | 0.88036 | -0.017583 | -0.016866 | -0.0629 | -0.0555 | 3.431
2490 | 1050 | 2.3714 | 0 | 0 | 0 | 117.393 | 35.6875 | 4.777 | 17.6266 | 0.86349 | -0.016866 | -0.016195 | -0.0555 | -0.0543 | 3.3224 | -0.046731 | -0.041697 | -0.0937 | -0.1543 | 2.9011 | -1.2103
2520 | 1080 | 2.3333 | 0 | 0 | 0 | 117.2143 | 35.6332 | 4.7227 | 17.6772 | 0.8473 | -0.016195 | -0.015565 | -0.0543 | -0.0285 | 2.5769
2550 | 1110 | 2.2973 | 0 | 0 | 0 | 117.1206 | 35.6047 | 4.6942 | 17.8445 | 0.83173 | -0.015565 | -0.014972 | -0.0285 | -0.0109 | 1.2689
2580 | 1140 | 2.2632 | 0 | 0 | 0 | 117.0847 | 35.5938 | 4.6833 | 17.9923 | 0.81676 | -0.014972 | -0.014415 | -0.0109 | -0.0475 | 2.036 | -0.041697 | -0.037465 | -0.1543 | -0.0858 | 2.9576 | -8.2514
2610 | 1170 | 2.2308 | 0 | 0 | 0 | 116.9285 | 35.5463 | 4.6358 | 18.0633 | 0.80235 | -0.014415 | -0.013889 | -0.0475 | -0.0108 | 2.013
2640 | 1200 | 2.2 | 0 | 0 | 0 | 116.893 | 35.5355 | 4.625 | 18.1881 | 0.78846 | -0.013889 | -0.013393 | -0.0108 | -0.096 | 4.0308
2670 | 1230 | 2.1707 | 0 | 0 | 0 | 116.5772 | 35.4395 | 4.529 | 18.244 | 0.77506 | -0.013393 | -0.012924 | -0.096 | -0.0206 | 4.3313 | -0.037465 | -0.03387 | -0.0858 | -0.1428 | 3.3017 | -25.547
2700 | 1260 | 2.1429 | 0 | 0 | 0 | 116.5094 | 35.4189 | 4.5084 | 18.3312 | 0.76214 | -0.012924 | -0.012481 | -0.0206 | -0.0172 | 1.4841
2730 | 1290 | 2.1163 | 0 | 0 | 0 | 116.4528 | 35.4017 | 4.4912 | 18.4484 | 0.74966 | -0.012481 | -0.01206 | -0.0172 | -0.048 | 2.7013
2760 | 1320 | 2.0909 | 0 | 0 | 0 | 116.2949 | 35.3537 | 4.4432 | 18.4959 | 0.7376 | -0.01206 | -0.011662 | -0.048 | -0.0488 | 4.084 | -0.03387 | -0.030785 | -0.1428 | -0.1323 | 4.2588 | -4.5858
2790 | 1350 | 2.0667 | 0 | 0 | 0 | 116.1344 | 35.3049 | 4.3944 | 18.5493 | 0.72594 | -0.011662 | -0.011284 | -0.0488 | -0.0463 | 4.1433
2820 | 1380 | 2.0435 | 0 | 0 | 0 | 115.9821 | 35.2586 | 4.3481 | 18.6783 | 0.71465 | -0.011284 | -0.010924 | -0.0463 | -0.0477 | 4.237
2850 | 1410 | 2.0213 | 0 | 0 | 0 | 115.8252 | 35.2109 | 4.3004 | 18.7249 | 0.70373 | -0.010924 | -0.010582 | -0.0477 | -0.0453 | 4.323 | -0.030785 | -0.028116 | -0.1323 | -0.1271 | 4.4141 | -5.8278
2880 | 1440 | 2 | 0 | 0 | 0 | 115.6762 | 35.1656 | 4.2551 | 18.4395 | 0.69315 | -0.010582 | -0.010257 | -0.0453 | -0.0425 | 4.2112
2910 | 1470 | 1.9796 | 0 | 0 | 0 | 115.5364 | 35.1231 | 4.2126 | 18.3677 | 0.68289 | -0.010257 | -0.0099462 | -0.0425 | -0.0445 | 4.3114
2940 | 1500 | 1.96 | 0 | 0 | 0 | 115.39 | 35.0786 | 4.1681 | 18.5187 | 0.67294 | -0.0099462 | -0.0096503 | -0.0445 | -0.046 | 4.6226 | -0.028116 | -0.64483 | -0.1271 | -4.041 | 4.5935 | #DIV/0!
2970 | 1530 | 1.9412 | 0 | 0 | 0 | 115.2387 | 35.0326 | 4.1221 | 18.5503 | 0.66329 | -0.0096503 | -0.0093678 | -0.046 | -0.0411 | 4.5742
3000 | 1560 | 1.9231 | 0 | 0 | 0 | 115.1035 | 34.9915 | 4.081 | 18.5874 | 0.65393 | -0.0093678 | -0.0090979 | -0.0411 | -0.04 | 4.3921
3030 | 1590 | 1.9057 | 0 | 0 | 0 | 114.9719 | 34.9515 | 4.041 | 18.5773 | 0.64483 | -0.0090979 | -0.0088398 | -0.04 | -0.0431 | 4.6396 | -0.64483 | 0 | -4.041 | 0 | #DIV/0! | #DIV/0!
3060 | 1620 | 1.8889 | 0 | 0 | 0 | 114.8301 | 34.9084 | 3.9979 | 18.6113 | 0.63599 | -0.0088398 | -0.008593 | -0.0431 | -0.039 | 4.7047
3090 | 1650 | 1.8727 | 0 | 0 | 0 | 114.7018 | 34.8694 | 3.9589 | 18.6348 | 0.6274 | -0.008593 | -0.6274 | -0.039 | -3.9589 | 4.5625
d2s/d(ln(t))2 ≈ 0.5 m

## Hydraulic Paramaters
Aquifer Hydraulic Paramaters | [12 empty] | Well Hydraulic Paramaters
| Theis Curve-Matching Method |  |  |  | Cooper-Jacob Straight Line Method |  |  |  | Theis Recovery Method |  |  |  |  | Long Term Yield (100 day method)
|  | Equations |  |  |  | Equations |  |  |  | Equations |  |  |  |  | Equations
| T = ( Q * W (u) ) / ( 4 * pi * s ) |  |  |  | T = ( 2.3 * Q ) / ( 4 * pi * slope ) |  |  |  | T = ( 2.3 * Q ) / ( 4 * pi * slope ) |  |  |  |  | Q100 = SAD*SC = 0.7*Available DD*Q/100 Day DD
Available DD = Well Depth - SWL - Pump Submergence
|  | Variables |  |  |  | Variables |  |  |  | Variables |  |  |  |  | Variables
| Note: Taken from radial flow time segment |  |  |  | Note: Taken from radial flow time segment |  |  |  | Note: Taken from radial flow time segment |  |  |  |  | Q (Discharge Rate) |  | 362.9 | m3/day
| (t=[301,697]) |  |  |  | (t=[301,697]) |  |  |  | (t'=[122,162]) |  |  |  |  | 100 Day DD |  | 41.5 | m
| Match Point |  |  |  | Slope is for 1 log10 cycle of time |  |  |  | Slope is for 1 log10 cycle of time |  |  |  |  | Well Depth |  | 91.4 | m
| s (Drawdown) |  | 20 | m | Q (Discharge Rate) |  | 362.9 | m3/day | [5 empty] | SWL |  | 30.91 | m
| t (time) |  | N/A | min | slope (ds/dlog(t)) |  | 13.5 | m | Q (Discharge Rate) |  | 362.9 | m3/day |  | Fracture depth |  | 76.8 | m
| W(u) |  | 3.3 |  | to (Intercept Time) |  | N/A |  | slope (ds/dlog(t)) |  | 7.5 | m
| 1/u |  | N/A |  | r (Radius) |  | N/A |  | to (Intercept Time) |  | N/A
[9 empty] | r (Radius) |  | N/A
| Q ((Discharge Rate) |  | 362.9 | m3/day
| r (Radius) |  | N/A | m
| T (Transmissivity) |  | 4.765 | m2/day | T (Transmissivity) |  | 4.92 | m2/day | T (Transmissivity) |  | 8.856 | m2/day |  | Q100 |  | 280.9 | m3/day
100 Day Drawdown = 41.5 m
100 Days
ds/d(log(t/t') = 7.5 m
Match Point
ds/d(log(t)) = 13.5 m