## Pumped Well Info
WELL, TEST, AQUIFER INFORMATION FOR PUMPING WELL
Well Information |  | Test Information |  | Aquifer Information
Well Name: | Mill Springs | Date of start of test (yyyy-mm-dd): | 2017-10-04 | Aquifer Number: | 203
Well ID Plate Number: | 21614 | Type of test (step test, constant rate test): | constant rate test | Aquifer Lithology | Westcoast Crystalline Complex
Well Tag Number: | 88224 | SWL at start of test (m): | 80.88 | Aquifer Type: | Fractured Bedrock
Well Location : | Mill Bay, BC | Reference datum for water level measurements (top of production casing): |  | Depth to upper-most water bearing fracture (m) | 131
UTM Zone (easting, northing): |  | Datalogger water level measurements?: | yes, SCADA
Well Casing Inside Diameter (mm): | 203 | Was a step-drawdown test performed before the constant rate test? | No

## Pumped Well Data
Pumped Well Data
WTN: | 88224 | SWL (m): | 80.88 |  | Average Pumping Rate (m3/day): |  |  | 518.4
Derivative is very noisy due to the excess of measuments. Derivative will be easier to interpret with a greater L-spacing inverval (3 was chosen)
Time since pumping started, t (min) | Time since pumping stopped, t' (min) | t/t' | Pumping rate, Q (USgpm) | Pumping rate, Q (L/s) | Pumping Rate, Q (m3/day) | Water Level (ft) | Water Level (m) | Drawdown or Residual Drawdown (m) | Extended Drawdown (m) | Adjusted Drawdown +0.1m/hr | ln(t) | Dt1 | Dt2 | Ds1 | Ds2 | ds/dt | Dt1 | Dt2 | Ds1 | Ds2 | ds/dt (L-Spacing = 3) | d2s/dt2
0 | - | - | 95 | 6 | 518.4 | 266.0523 | 80.88 | 0 | 0 | 0 | #NUM! | #NUM! | #NUM! | #VALUE! | 1.17 | #VALUE!
0.5 | - | - | 95 | 6 | 518.4 | 269.901 | 82.05 | 1.17 | 1.17 | 1.1708 | -0.69315 | #NUM! | 0.69315 | 1.17 | 0 | #NUM!
1 | - | - | 95 | 6 | 518.4 | 269.901 | 82.05 | 1.17 | 1.17 | 1.1717 | 0 | 0.69315 | 0.40547 | 0 | 0.05 | 0.077803 | 0.91629 | 0.47 | 0.09 | -0.01 | 0.019238 | 0.25725
1.5 | - | - | 95 | 6 | 518.4 | 270.0655 | 82.1 | 1.22 | 1.22 | 1.2225 | 0.40547 | 0.40547 | 0.28768 | 0.05 | 0.04 | 0.13251
2 | - | - | 95 | 6 | 518.4 | 270.1971 | 82.14 | 1.26 | 1.26 | 1.2633 | 0.69315 | 0.28768 | 0.22314 | 0.04 | 0 | 0.060738
2.5 | - | - | 95 | 6 | 518.4 | 270.1971 | 82.14 | 1.26 | 1.26 | 1.2642 | 0.91629 | 0.22314 | 0.18232 | 0 | -0.1 | -0.30185 | 0.47 | 0.40547 | -0.01 | 0.2 | 0.25496 | 0.19218
3 | - | - | 95 | 6 | 518.4 | 269.8681 | 82.04 | 1.16 | 1.16 | 1.165 | 1.0986 | 0.18232 | 0.15415 | -0.1 | 0.01 | -0.21613
3.5 | - | - | 95 | 6 | 518.4 | 269.901 | 82.05 | 1.17 | 1.17 | 1.1758 | 1.2528 | 0.15415 | 0.13353 | 0.01 | 0.08 | 0.35114
4 | - | - | 95 | 6 | 518.4 | 270.1642 | 82.13 | 1.25 | 1.25 | 1.2567 | 1.3863 | 0.13353 | 0.11778 | 0.08 | 0.09 | 0.68678 | 0.40547 | 0.40547 | 0.2 | 0.08 | 0.34528 | -0.11701
4.5 | - | - | 95 | 6 | 518.4 | 270.4602 | 82.22 | 1.34 | 1.34 | 1.3475 | 1.5041 | 0.11778 | 0.10536 | 0.09 | 0.07 | 0.71148
5 | - | - | 95 | 6 | 518.4 | 270.6905 | 82.29 | 1.41 | 1.41 | 1.4183 | 1.6094 | 0.10536 | 0.18232 | 0.07 | 0.04 | 0.50141
6 | - | - | 95 | 6 | 518.4 | 270.8221 | 82.33 | 1.45 | 1.45 | 1.46 | 1.7918 | 0.18232 | 0.15415 | 0.04 | 0 | 0.10051 | 0.40547 | 0.44183 | 0.08 | 0.18 | 0.29784 | 0.51771
7 | - | - | 95 | 6 | 518.4 | 270.8221 | 82.33 | 1.45 | 1.45 | 1.4617 | 1.9459 | 0.15415 | 0.13353 | 0 | 0.03 | 0.12038
8 | - | - | 95 | 6 | 518.4 | 270.9207 | 82.36 | 1.48 | 1.48 | 1.4933 | 2.0794 | 0.13353 | 0.11778 | 0.03 | 0.05 | 0.33085
9 | - | - | 95 | 6 | 518.4 | 271.0852 | 82.41 | 1.53 | 1.53 | 1.545 | 2.1972 | 0.11778 | 0.10536 | 0.05 | 0.04 | 0.40083 | 0.44183 | 0.35667 | 0.18 | 0.21 | 0.50775 | 0.29438
10 | - | - | 95 | 6 | 518.4 | 271.2168 | 82.45 | 1.57 | 1.57 | 1.5867 | 2.3026 | 0.10536 | 0.18232 | 0.04 | 0.08 | 0.40131
12 | - | - | 95 | 6 | 518.4 | 271.48 | 82.53 | 1.65 | 1.65 | 1.67 | 2.4849 | 0.18232 | 0.15415 | 0.08 | 0.06 | 0.41193
14 | - | - | 95 | 6 | 518.4 | 271.6773 | 82.59 | 1.71 | 1.71 | 1.7333 | 2.6391 | 0.15415 | 0.13353 | 0.06 | 0.07 | 0.46156 | 0.35667 | 0.55962 | 0.21 | 0.4 | 0.63782 | 0.52809
16 | - | - | 95 | 6 | 518.4 | 271.9076 | 82.66 | 1.78 | 1.78 | 1.8067 | 2.7726 | 0.13353 | 0.11778 | 0.07 | 0.07 | 0.56146
18 | - | - | 95 | 6 | 518.4 | 272.1379 | 82.73 | 1.85 | 1.85 | 1.88 | 2.8904 | 0.11778 | 0.10536 | 0.07 | 0.07 | 0.6313
20 | - | - | 95 | 6 | 518.4 | 272.3681 | 82.8 | 1.92 | 1.92 | 1.9533 | 2.9957 | 0.10536 | 0.22314 | 0.07 | 0.14 | 0.65252 | 0.55962 | 0.35667 | 0.4 | 0.32 | 0.82617 | 0.34038
25 | - | - | 95 | 6 | 518.4 | 272.8286 | 82.94 | 2.06 | 2.06 | 2.1017 | 3.2189 | 0.22314 | 0.18232 | 0.14 | 0.13 | 0.67452
30 | - | - | 95 | 6 | 518.4 | 273.2563 | 83.07 | 2.19 | 2.19 | 2.24 | 3.4012 | 0.18232 | 0.15415 | 0.13 | 0.13 | 0.78363
35 | - | - | 95 | 6 | 518.4 | 273.6839 | 83.2 | 2.32 | 2.32 | 2.3783 | 3.5553 | 0.15415 | 0.13353 | 0.13 | 0.1 | 0.79272 | 0.35667 | 0.33647 | 0.32 | 0.38 | 1.0167 | 0.64868
40 | - | - | 95 | 6 | 518.4 | 274.0129 | 83.3 | 2.42 | 2.42 | 2.4867 | 3.6889 | 0.13353 | 0.11778 | 0.1 | 0.11 | 0.8472
45 | - | - | 95 | 6 | 518.4 | 274.3747 | 83.41 | 2.53 | 2.53 | 2.605 | 3.8067 | 0.11778 | 0.10536 | 0.11 | 0.11 | 0.99204
50 | - | - | 95 | 6 | 518.4 | 274.7365 | 83.52 | 2.64 | 2.64 | 2.7233 | 3.912 | 0.10536 | 0.09531 | 0.11 | 0.1 | 1.0467 | 0.33647 | 0.35667 | 0.38 | 0.49 | 1.248 | 0.94976
55 | - | - | 95 | 6 | 518.4 | 275.0655 | 83.62 | 2.74 | 2.74 | 2.8317 | 4.0073 | 0.09531 | 0.087011 | 0.1 | 0.1 | 1.1015
60 | - | - | 95 | 6 | 518.4 | 275.3944 | 83.72 | 2.84 | 2.84 | 2.94 | 4.0943 | 0.087011 | 0.15415 | 0.1 | 0.18 | 1.1559
70 | - | - | 95 | 6 | 518.4 | 275.9865 | 83.9 | 3.02 | 3.02 | 3.1367 | 4.2485 | 0.15415 | 0.13353 | 0.18 | 0.16 | 1.184 | 0.35667 | 0.64185 | 0.49 | 1.23 | 1.5676 | 2.3611
80 | - | - | 95 | 6 | 518.4 | 276.5128 | 84.06 | 3.18 | 3.18 | 3.3133 | 4.382 | 0.13353 | 0.11778 | 0.16 | 0.18 | 1.3736
90 | - | - | 95 | 6 | 518.4 | 277.105 | 84.24 | 3.36 | 3.36 | 3.51 | 4.4998 | 0.11778 | 0.10536 | 0.18 | 0.15 | 1.473
100 | - | - | 95 | 6 | 518.4 | 277.5984 | 84.39 | 3.51 | 3.51 | 3.6767 | 4.6052 | 0.10536 | 0.26236 | 0.15 | 0.45 | 1.5072 | 0.64185 | 0.38777 | 1.23 | 1.05 | 2.4097 | 1.0133
130 | - | - | 95 | 6 | 518.4 | 279.0786 | 84.84 | 3.96 | 3.96 | 4.1767 | 4.8675 | 0.26236 | 0.20764 | 0.45 | 0.41 | 1.86
160 | - | - | 95 | 6 | 518.4 | 280.4273 | 85.25 | 4.37 | 4.37 | 4.6367 | 5.0752 | 0.20764 | 0.17185 | 0.41 | 0.37 | 2.0722
190 | - | - | 95 | 6 | 518.4 | 281.6444 | 85.62 | 4.74 | 4.74 | 5.0567 | 5.247 | 0.17185 | 0.1466 | 0.37 | 0.34 | 2.2427 | 0.38777 | 0.429 | 1.05 | 1.48 | 3.0601 | 1.9546
220 | - | - | 95 | 6 | 518.4 | 282.7628 | 85.96 | 5.08 | 5.08 | 5.4467 | 5.3936 | 0.1466 | 0.12783 | 0.34 | 0.38 | 2.6682
250 | - | - | 95 | 6 | 518.4 | 284.0128 | 86.34 | 5.46 | 5.46 | 5.8767 | 5.5215 | 0.12783 | 0.11333 | 0.38 | 0.33 | 2.9404
280 | - | - | 95 | 6 | 518.4 | 285.0984 | 86.67 | 5.79 | 5.79 | 6.2567 | 5.6348 | 0.11333 | 0.10178 | 0.33 | 0.32 | 3.0341 | 0.429 | 0.34967 | 1.48 | 1.44 | 3.8181 | 1.6591
310 | - | - | 95 | 6 | 518.4 | 286.151 | 86.99 | 6.11 | 6.11 | 6.6267 | 5.7366 | 0.10178 | 0.17693 | 0.32 | 0.58 | 3.1929
370 | - | - | 95 | 6 | 518.4 | 288.0589 | 87.57 | 6.69 | 6.69 | 7.3067 | 5.9135 | 0.17693 | 0.15028 | 0.58 | 0.58 | 3.5924
430 | - | - | 95 | 6 | 518.4 | 289.9668 | 88.15 | 7.27 | 7.27 | 7.9867 | 6.0638 | 0.15028 | 0.13062 | 0.58 | 0.52 | 3.9245 | 0.34967 | 0.25857 | 1.44 | 1.25 | 4.5298 | 2.0955
490 | - | - | 95 | 6 | 518.4 | 291.6773 | 88.67 | 7.79 | 7.79 | 8.6067 | 6.1944 | 0.13062 | 0.11551 | 0.52 | 0.49 | 4.1195
550 | - | - | 95 | 6 | 518.4 | 293.2891 | 89.16 | 8.28 | 8.28 | 9.1967 | 6.3099 | 0.11551 | 0.10354 | 0.49 | 0.43 | 4.195
610 | - | - | 95 | 6 | 518.4 | 294.7036 | 89.59 | 8.71 | 8.71 | 9.7267 | 6.4135 | 0.10354 | 0.093819 | 0.43 | 0.45 | 4.4906 | 0.25857 | 0.20526 | 1.25 | 1.15 | 5.2625 | 3.7533
670 | - | - | 95 | 6 | 518.4 | 296.1839 | 90.04 | 9.16 | 9.16 | 10.2767 | 6.5073 | 0.093819 | 0.085767 | 0.45 | 0.44 | 4.9708
730 | - | - | 95 | 6 | 518.4 | 297.6312 | 90.48 | 9.6 | 9.6 | 10.8167 | 6.593 | 0.085767 | 0.078988 | 0.44 | 0.36 | 4.8321
790 | - | - | 95 | 6 | 518.4 | 298.8155 | 90.84 | 9.96 | 9.96 | 11.2767 | 6.672 | 0.078988 | 0.073203 | 0.36 | 0.4 | 5.0282 | 0.20526 | 0.17022 | 1.15 | 1.15 | 6.2331 | 3.4068
850 | - | - | 95 | 6 | 518.4 | 300.1312 | 91.24 | 10.36 | 10.36 | 11.7767 | 6.7452 | 0.073203 | 0.068208 | 0.4 | 0.37 | 5.4437
910 | - | - | 95 | 6 | 518.4 | 301.3483 | 91.61 | 10.73 | 10.73 | 12.2467 | 6.8134 | 0.068208 | 0.063851 | 0.37 | 0.38 | 5.6966
970 | - | - | 95 | 6 | 518.4 | 302.5983 | 91.99 | 11.11 | 11.11 | 12.7267 | 6.8773 | 0.063851 | 0.060018 | 0.38 | 0.33 | 5.7178 | 0.17022 | 0.14542 | 1.15 | 1.03 | 6.9324 | 2.3914
1030 | - | - | 95 | 6 | 518.4 | 303.6839 | 92.32 | 11.44 | 11.44 | 13.1567 | 6.9373 | 0.060018 | 0.056619 | 0.33 | 0.42 | 6.4862
1090 | - | - | 95 | 6 | 518.4 | 305.0654 | 92.74 | 11.86 | 11.86 | 13.6767 | 6.9939 | 0.056619 | 0.053584 | 0.42 | 0.4 | 7.4421
1150 | - | - | 95 | 6 | 518.4 | 306.3812 | 93.14 | 12.26 | 12.26 | 14.1767 | 7.0475 | 0.053584 | 0.050858 | 0.4 | 0.37 | 7.3675 | 0.14542 | 0.12693 | 1.03 | 0.96 | 7.3394 | 1.1583
1210 | - | - | 95 | 6 | 518.4 | 307.5983 | 93.51 | 12.63 | 12.63 | 14.6467 | 7.0984 | 0.050858 | 0.048397 | 0.37 | 0.34 | 7.1471
1270 | - | - | 95 | 6 | 518.4 | 308.7168 | 93.85 | 12.97 | 12.97 | 15.0867 | 7.1468 | 0.048397 | 0.046162 | 0.34 | 0.32 | 6.9776
1330 | - | - | 95 | 6 | 518.4 | 309.7694 | 94.17 | 13.29 | 13.29 | 15.5067 | 7.1929 | 0.046162 | 0.044125 | 0.32 | 0.34 | 7.3275 | 0.12693 | 0.11262 | 0.96 | 0.84 | 7.5079 | 0.64225
1390 | - | - | 95 | 6 | 518.4 | 310.8878 | 94.51 | 13.63 | 13.63 | 15.9467 | 7.2371 | 0.044125 | 0.04226 | 0.34 | 0.31 | 7.5165
1450 | - | - | 95 | 6 | 518.4 | 311.9075 | 94.82 | 13.94 | 13.94 | 16.3567 | 7.2793 | 0.04226 | 0.040546 | 0.31 | 0.31 | 7.4938
1510 | - | - | 95 | 6 | 518.4 | 312.9273 | 95.13 | 14.25 | 14.25 | 16.7667 | 7.3199 | 0.040546 | 0.038966 | 0.31 | 0.31 | 7.8037 | 0.11262 | 0.10121 | 0.84 | 0.78 | 7.5894 | 3.6622
1570 | - | - | 95 | 6 | 518.4 | 313.947 | 95.44 | 14.56 | 14.56 | 17.1767 | 7.3588 | 0.038966 | 0.037504 | 0.31 | 0.28 | 7.706
1630 | - | - | 95 | 6 | 518.4 | 314.8681 | 95.72 | 14.84 | 14.84 | 17.5567 | 7.3963 | 0.037504 | 0.036149 | 0.28 | 0.25 | 7.1858
1690 | - | - | 95 | 6 | 518.4 | 315.6904 | 95.97 | 15.09 | 15.09 | 17.9067 | 7.4325 | 0.036149 | 0.034887 | 0.25 | 0.27 | 7.3349 | 0.10121 | 0.091901 | 0.78 | 0.76 | 8.0018 | 4.7309
1750 | - | - | 95 | 6 | 518.4 | 316.5786 | 96.24 | 15.36 | 15.36 | 18.2767 | 7.4674 | 0.034887 | 0.033711 | 0.27 | 0.25 | 7.5748
1810 | - | - | 95 | 6 | 518.4 | 317.401 | 96.49 | 15.61 | 15.61 | 18.6267 | 7.5011 | 0.033711 | 0.032612 | 0.25 | 0.26 | 7.6989
1870 | - | - | 95 | 6 | 518.4 | 318.2562 | 96.75 | 15.87 | 15.87 | 18.9867 | 7.5337 | 0.032612 | 0.031582 | 0.26 | 0.27 | 8.2656 | 0.091901 | 0.084162 | 0.76 | 0.73 | 8.4806 | -4.7021
1930 | - | - | 95 | 6 | 518.4 | 319.1444 | 97.02 | 16.14 | 16.14 | 19.3567 | 7.5653 | 0.031582 | 0.030615 | 0.27 | 0.23 | 8.023
1990 | - | - | 95 | 6 | 518.4 | 319.901 | 97.25 | 16.37 | 16.37 | 19.6867 | 7.5959 | 0.030615 | 0.029705 | 0.23 | 0.26 | 8.1421
2050 | - | - | 95 | 6 | 518.4 | 320.7562 | 97.51 | 16.63 | 16.63 | 20.0467 | 7.6256 | 0.029705 | 0.028848 | 0.26 | 0.25 | 8.7087 | 0.084162 | 0.077625 | 0.73 | 0.58 | 8.0485 | 6.9912
2110 | - | - | 95 | 6 | 518.4 | 321.5786 | 97.76 | 16.88 | 16.88 | 20.3967 | 7.6544 | 0.028848 | 0.028039 | 0.25 | 0.21 | 8.0694
2170 | - | - | 95 | 6 | 518.4 | 322.2694 | 97.97 | 17.09 | 17.09 | 20.7067 | 7.6825 | 0.028039 | 0.027274 | 0.21 | 0.27 | 8.7111
2230 | - | - | 95 | 6 | 518.4 | 323.1575 | 98.24 | 17.36 | 17.36 | 21.0767 | 7.7098 | 0.027274 | 0.02655 | 0.27 | 0.19 | 8.5094 | 0.077625 | 0.072031 | 0.58 | 0.7 | 8.6369 | 14.6271
2290 | - | - | 95 | 6 | 518.4 | 323.7825 | 98.43 | 17.55 | 17.55 | 21.3667 | 7.7363 | 0.02655 | 0.025864 | 0.19 | 0.18 | 7.0566
2350 | - | - | 95 | 6 | 518.4 | 324.3746 | 98.61 | 17.73 | 17.73 | 21.6467 | 7.7622 | 0.025864 | 0.025211 | 0.18 | 0.21 | 7.6533
2410 | - | - | 95 | 6 | 518.4 | 325.0654 | 98.82 | 17.94 | 17.94 | 21.9567 | 7.7874 | 0.025211 | 0.024591 | 0.21 | 0.19 | 8.0242 | 0.072031 | 0.067189 | 0.7 | 0.66 | 9.7723 | 4.2967
2470 | - | - | 95 | 6 | 518.4 | 325.6904 | 99.01 | 18.13 | 18.13 | 22.2467 | 7.812 | 0.024591 | 0.024001 | 0.19 | 0.22 | 8.455
2530 | - | - | 95 | 6 | 518.4 | 326.4141 | 99.23 | 18.35 | 18.35 | 22.5667 | 7.836 | 0.024001 | 0.023439 | 0.22 | 0.29 | 10.7885
2590 | - | - | 95 | 6 | 518.4 | 327.3681 | 99.52 | 18.64 | 18.64 | 22.9567 | 7.8594 | 0.023439 | 0.022902 | 0.29 | 0.23 | 11.1943 | 0.067189 | 0.062958 | 0.66 | 0.65 | 10.0818 | -17.2998
2650 | - | - | 95 | 6 | 518.4 | 328.1246 | 99.75 | 18.87 | 18.87 | 23.2867 | 7.8823 | 0.022902 | 0.022389 | 0.23 | 0.21 | 9.7075
2710 | - | - | 95 | 6 | 518.4 | 328.8154 | 99.96 | 19.08 | 19.08 | 23.5967 | 7.9047 | 0.022389 | 0.021899 | 0.21 | 0.22 | 9.7166
2770 | - | - | 95 | 6 | 518.4 | 329.5391 | 100.18 | 19.3 | 19.3 | 23.9167 | 7.9266 | 0.021899 | 0.021429 | 0.22 | 0.2 | 9.6858 | 0.062958 | 0.059228 | 0.65 | 0.45 | 8.9195 | -17.3154
2830 | - | - | 95 | 6 | 518.4 | 330.197 | 100.38 | 19.5 | 19.5 | 24.2167 | 7.948 | 0.021429 | 0.02098 | 0.2 | 0.2 | 9.434
2890 | - | - | 95 | 6 | 518.4 | 330.8549 | 100.58 | 19.7 | 19.7 | 24.5167 | 7.969 | 0.02098 | 0.020549 | 0.2 | 0.25 | 10.8633
2950 | - | - | 95 | 6 | 518.4 | 331.6773 | 100.83 | 19.95 | 19.95 | 24.8667 | 7.9896 | 0.020549 | 0.020135 | 0.25 | 0.1 | 8.5298 | 0.059228 | 0.055915 | 0.45 | 0.45 | 7.8293 | 14.1442
3010 | - | - | 95 | 6 | 518.4 | 332.0062 | 100.93 | 20.05 | 20.05 | 25.0667 | 8.0097 | 0.020135 | 0.019737 | 0.1 | 0.18 | 7.0638
3070 | - | - | 95 | 6 | 518.4 | 332.5983 | 101.11 | 20.23 | 20.23 | 25.3467 | 8.0294 | 0.019737 | 0.019355 | 0.18 | 0.17 | 8.9497
3130 | - | - | 95 | 6 | 518.4 | 333.1575 | 101.28 | 20.4 | 20.4 | 25.6167 | 8.0488 | 0.019355 | 0.018988 | 0.17 | 0.16 | 8.603 | 0.055915 | 0.052954 | 0.45 | 0.49 | 8.667 | 16.806
3190 | - | - | 95 | 6 | 518.4 | 333.6838 | 101.44 | 20.56 | 20.56 | 25.8767 | 8.0678 | 0.018988 | 0.018634 | 0.16 | 0.14 | 7.9655
3250 | - | - | 95 | 6 | 518.4 | 334.1444 | 101.58 | 20.7 | 20.7 | 26.1167 | 8.0864 | 0.018634 | 0.018293 | 0.14 | 0.15 | 7.8596
3310 | - | - | 95 | 6 | 518.4 | 334.6378 | 101.73 | 20.85 | 20.85 | 26.3667 | 8.1047 | 0.018293 | 0.017965 | 0.15 | 0.16 | 8.5563 | 0.052954 | 0.05029 | 0.49 | 0.5 | 9.6068 | -4.9877
3370 | - | - | 95 | 6 | 518.4 | 335.1641 | 101.89 | 21.01 | 21.01 | 26.6267 | 8.1227 | 0.017965 | 0.017648 | 0.16 | 0.17 | 9.273
3430 | - | - | 95 | 6 | 518.4 | 335.7233 | 102.06 | 21.18 | 21.18 | 26.8967 | 8.1403 | 0.017648 | 0.017341 | 0.17 | 0.16 | 9.428
3490 | - | - | 95 | 6 | 518.4 | 336.2496 | 102.22 | 21.34 | 21.34 | 27.1567 | 8.1577 | 0.017341 | 0.017046 | 0.16 | 0.16 | 9.3071 | 0.05029 | 0.047881 | 0.5 | 0.42 | 9.3426 | -9.3064
3550 | - | - | 95 | 6 | 518.4 | 336.7759 | 102.38 | 21.5 | 21.5 | 27.4167 | 8.1747 | 0.017046 | 0.01676 | 0.16 | 0.18 | 10.0688
3610 | - | - | 95 | 6 | 518.4 | 337.368 | 102.56 | 21.68 | 21.68 | 27.6967 | 8.1915 | 0.01676 | 0.016484 | 0.18 | 0.16 | 10.2188
3670 | - | - | 95 | 6 | 518.4 | 337.8944 | 102.72 | 21.84 | 21.84 | 27.9567 | 8.2079 | 0.016484 | 0.016217 | 0.16 | 0.15 | 9.4763 | 0.047881 | 0.045693 | 0.42 | 0.41 | 8.8746 | 6.4299
3730 | - | - | 95 | 6 | 518.4 | 338.3878 | 102.87 | 21.99 | 21.99 | 28.2067 | 8.2242 | 0.016217 | 0.015958 | 0.15 | 0.14 | 9.0096
3790 | - | - | 95 | 6 | 518.4 | 338.8483 | 103.01 | 22.13 | 22.13 | 28.4467 | 8.2401 | 0.015958 | 0.015707 | 0.14 | 0.13 | 8.5229
3850 | - | - | 95 | 6 | 518.4 | 339.2759 | 103.14 | 22.26 | 22.26 | 28.6767 | 8.2558 | 0.015707 | 0.015464 | 0.13 | 0.14 | 8.6679 | 0.045693 | 0.043696 | 0.41 | 0.41 | 9.1825 | #VALUE!
3910 | - | - | 95 | 6 | 518.4 | 339.7365 | 103.28 | 22.4 | 22.4 | 28.9167 | 8.2713 | 0.015464 | 0.015229 | 0.14 | 0.12 | 8.462
3970 | - | - | 95 | 6 | 518.4 | 340.1312 | 103.4 | 22.52 | 22.52 | 29.1367 | 8.2865 | 0.015229 | 0.015 | 0.12 | 0.15 | 8.9478
4030 | - | - | 95 | 6 | 518.4 | 340.6246 | 103.55 | 22.67 | 22.67 | 29.3867 | 8.3015 | 0.015 | 0.014779 | 0.15 | 0.14 | 9.7345 | 0.043696 | #VALUE! | 0.41 | -0.47 | #VALUE! | #VALUE!
4090 | - | - | 95 | 6 | 518.4 | 341.0851 | 103.69 | 22.81 | 22.81 | 29.6267 | 8.3163 | 0.014779 | 0.014563 | 0.14 | 0.13 | 9.1978
4150 | - | - | 95 | 6 | 518.4 | 341.5128 | 103.82 | 22.94 | 22.94 | 29.8567 | 8.3309 | 0.014563 | 0.014354 | 0.13 | 0.14 | 9.3428
4210 | - | - | 95 | 6 | 518.4 | 341.9733 | 103.96 | 23.08 | 23.08 | 30.0967 | 8.3452 | 0.014354 | 0.014151 | 0.14 | 0.13 | 9.4678 | #VALUE! | #VALUE! | -0.47 | -0.08 | #VALUE! | #VALUE!
4270 | - | - | 95 | 6 | 518.4 | 342.4009 | 104.09 | 23.21 | 23.21 | 30.3267 | 8.3594 | 0.014151 | 0.011642 | 0.13 | 0.11 | 9.3305
4320 | - | - | 95 | 6 | 518.4 | 342.7628 | 104.2 | 23.32 | 23.32 | 30.52 | 8.371 | 0.011642 | #VALUE! | 0.11 | -0.71 | #VALUE!
4320.5 | 0.5 | #NAME? | 0 | 0 | 0 | 340.4273 | 103.49 | 22.61 | 23.78 |  | ln(t/t') | D(t/t')1 | D(t/t')2 | Ds1 | Ds2 | ds/d(t/t') | D(t/t')1 | D(t/t')2 | Ds1 | Ds2 | ds/d(t/t') (L-Spacing = 3) | d2s/d(t/t')2
4321 | 1 | 4321 | 0 | 0 | 0 | 340.3286 | 103.46 | 22.58 | 23.75 |  | 8.3712 | #VALUE! | -0.40535 | -0.03 | -0.02 | #VALUE! | -0.91594 | -0.46966 | -0.08 | -0.06 | 0.11406 | 0.041385
4321.5 | 1.5 | 2881 | 0 | 0 | 0 | 340.2628 | 103.44 | 22.56 | 23.78 |  | 7.9659 | -0.40535 | -0.28757 | -0.02 | -0.03 | 0.081505
4322 | 2 | 2161 | 0 | 0 | 0 | 340.1641 | 103.41 | 22.53 | 23.79 |  | 7.6783 | -0.28757 | -0.22303 | -0.03 | -0.03 | 0.12133
4322.5 | 2.5 | 1729 | 0 | 0 | 0 | 340.0654 | 103.38 | 22.5 | 23.76 |  | 7.4553 | -0.22303 | -0.18221 | -0.03 | -0.02 | 0.12089 | -0.46966 | -0.405 | -0.06 | -0.07 | 0.15196 | 0.12348
4323 | 3 | 1441 | 0 | 0 | 0 | 339.9996 | 103.36 | 22.48 | 23.64 |  | 7.2731 | -0.18221 | -0.15404 | -0.02 | -0.02 | 0.12064
4323.5 | 3.5 | 1235.2857 | 0 | 0 | 0 | 339.9338 | 103.34 | 22.46 | 23.63 |  | 7.1191 | -0.15404 | -0.13342 | -0.02 | -0.02 | 0.14059
4324 | 4 | 1081 | 0 | 0 | 0 | 339.868 | 103.32 | 22.44 | 23.69 |  | 6.9856 | -0.13342 | -0.11767 | -0.02 | -0.02 | 0.16057 | -0.405 | -0.40477 | -0.07 | -0.1 | 0.20996 | 0.1751
4324.5 | 4.5 | 961 | 0 | 0 | 0 | 339.8023 | 103.3 | 22.42 | 23.76 |  | 6.868 | -0.11767 | -0.10524 | -0.02 | -0.02 | 0.18056
4325 | 5 | 865 | 0 | 0 | 0 | 339.7365 | 103.28 | 22.4 | 23.81 |  | 6.7627 | -0.10524 | -0.18209 | -0.02 | -0.03 | 0.18077
4326 | 6 | 721 | 0 | 0 | 0 | 339.6378 | 103.25 | 22.37 | 23.82 |  | 6.5806 | -0.18209 | -0.15392 | -0.03 | -0.04 | 0.2163 | -0.40477 | -0.44068 | -0.1 | -0.14 | 0.28087 | 0.27239
4327 | 7 | 618.1429 | 0 | 0 | 0 | 339.5062 | 103.21 | 22.33 | 23.78 |  | 6.4267 | -0.15392 | -0.1333 | -0.04 | -0.03 | 0.24122
4328 | 8 | 541 | 0 | 0 | 0 | 339.4075 | 103.18 | 22.3 | 23.78 |  | 6.2934 | -0.1333 | -0.11755 | -0.03 | -0.03 | 0.24108
4329 | 9 | 481 | 0 | 0 | 0 | 339.3088 | 103.15 | 22.27 | 23.8 |  | 6.1759 | -0.11755 | -0.10513 | -0.03 | -0.03 | 0.27113 | -0.44068 | -0.35529 | -0.14 | -0.16 | 0.39113 | 0.29267
4330 | 10 | 433 | 0 | 0 | 0 | 339.2101 | 103.12 | 22.24 | 23.81 |  | 6.0707 | -0.10513 | -0.18186 | -0.03 | -0.06 | 0.30169
4332 | 12 | 361 | 0 | 0 | 0 | 339.0128 | 103.06 | 22.18 | 23.83 |  | 5.8889 | -0.18186 | -0.15369 | -0.06 | -0.05 | 0.32744
4334 | 14 | 309.5714 | 0 | 0 | 0 | 338.8483 | 103.01 | 22.13 | 23.84 |  | 5.7352 | -0.15369 | -0.13307 | -0.05 | -0.06 | 0.39263 | -0.35529 | -0.55617 | -0.16 | -0.35 | 0.5201 | 0.63731
4336 | 16 | 271 | 0 | 0 | 0 | 338.6509 | 102.95 | 22.07 | 23.85 |  | 5.6021 | -0.13307 | -0.11732 | -0.06 | -0.05 | 0.43776
4338 | 18 | 241 | 0 | 0 | 0 | 338.4865 | 102.9 | 22.02 | 23.87 |  | 5.4848 | -0.11732 | -0.1049 | -0.05 | -0.05 | 0.45282
4340 | 20 | 217 | 0 | 0 | 0 | 338.322 | 102.85 | 21.97 | 23.89 |  | 5.3799 | -0.1049 | -0.22199 | -0.05 | -0.12 | 0.49716 | -0.55617 | -0.35324 | -0.35 | -0.29 | 0.74653 | 0.32242
4345 | 25 | 173.8 | 0 | 0 | 0 | 337.9273 | 102.73 | 21.85 | 23.91 |  | 5.1579 | -0.22199 | -0.18117 | -0.12 | -0.12 | 0.60762
4350 | 30 | 145 | 0 | 0 | 0 | 337.5325 | 102.61 | 21.73 | 23.92 |  | 4.9767 | -0.18117 | -0.153 | -0.12 | -0.11 | 0.69304
4355 | 35 | 124.4286 | 0 | 0 | 0 | 337.1707 | 102.5 | 21.62 | 23.94 |  | 4.8237 | -0.153 | -0.13238 | -0.11 | -0.1 | 0.73848 | -0.35324 | -0.33191 | -0.29 | -0.34 | 0.92585 | 0.87616
4360 | 40 | 109 | 0 | 0 | 0 | 336.8417 | 102.4 | 21.52 | 23.94 |  | 4.6913 | -0.13238 | -0.11664 | -0.1 | -0.1 | 0.80959
4365 | 45 | 97 | 0 | 0 | 0 | 336.5128 | 102.3 | 21.42 | 23.95 |  | 4.5747 | -0.11664 | -0.10422 | -0.1 | -0.09 | 0.86065
4370 | 50 | 87.4 | 0 | 0 | 0 | 336.2167 | 102.21 | 21.33 | 23.97 |  | 4.4705 | -0.10422 | -0.094167 | -0.09 | -0.1 | 0.96779 | -0.33191 | -0.34986 | -0.34 | -0.51 | 1.2353 | 1.9854
4375 | 55 | 79.5455 | 0 | 0 | 0 | 335.8878 | 102.11 | 21.23 | 23.97 |  | 4.3763 | -0.094167 | -0.085869 | -0.1 | -0.09 | 1.0547
4380 | 60 | 73 | 0 | 0 | 0 | 335.5917 | 102.02 | 21.14 | 23.98 |  | 4.2905 | -0.085869 | -0.15187 | -0.09 | -0.15 | 1.0263
4390 | 70 | 62.7143 | 0 | 0 | 0 | 335.0983 | 101.87 | 20.99 | 24.01 |  | 4.1386 | -0.15187 | -0.13126 | -0.15 | -0.2 | 1.2752 | -0.34986 | -0.6217 | -0.51 | -1.66 | 1.8943 | 5.2296
4400 | 80 | 55 | 0 | 0 | 0 | 334.4404 | 101.67 | 20.79 | 23.97 |  | 4.0073 | -0.13126 | -0.11551 | -0.2 | -0.15 | 1.404
4410 | 90 | 49 | 0 | 0 | 0 | 333.947 | 101.52 | 20.64 | 24 |  | 3.8918 | -0.11551 | -0.1031 | -0.15 | -0.16 | 1.4325
4420 | 100 | 44.2 | 0 | 0 | 0 | 333.4207 | 101.36 | 20.48 | 23.99 |  | 3.7887 | -0.1031 | -0.2556 | -0.16 | -0.42 | 1.5782 | -0.6217 | -0.36801 | -1.66 | -1.6 | 3.7239 | 1.9282
4450 | 130 | 34.2308 | 0 | 0 | 0 | 332.0391 | 100.94 | 20.06 | 24.02 |  | 3.5331 | -0.2556 | -0.20092 | -0.42 | -0.64 | 2.5066
4480 | 160 | 28 | 0 | 0 | 0 | 329.9338 | 100.3 | 19.42 | 23.79 |  | 3.3322 | -0.20092 | -0.16518 | -0.64 | -0.6 | 3.4307
4510 | 190 | 23.7368 | 0 | 0 | 0 | 327.9602 | 99.7 | 18.82 | 23.56 |  | 3.167 | -0.16518 | -0.13997 | -0.6 | -0.6 | 3.9865 | -0.36801 | -0.39691 | -1.6 | -2.2 | 4.9227 | 2.5024
4540 | 220 | 20.6364 | 0 | 0 | 0 | 325.9865 | 99.1 | 18.22 | 23.3 |  | 3.0271 | -0.13997 | -0.12125 | -0.6 | -0.5 | 4.1993
4570 | 250 | 18.28 | 0 | 0 | 0 | 324.3417 | 98.6 | 17.72 | 23.18 |  | 2.9058 | -0.12125 | -0.10679 | -0.5 | -0.5 | 4.4208
4600 | 280 | 16.4286 | 0 | 0 | 0 | 322.697 | 98.1 | 17.22 | 23.01 |  | 2.799 | -0.10679 | -0.095282 | -0.5 | -0.5 | 4.981 | -0.39691 | -0.31248 | -2.2 | -1.9 | 5.8436 | 3.5412
4630 | 310 | 14.9355 | 0 | 0 | 0 | 321.0523 | 97.6 | 16.72 | 22.83 |  | 2.7037 | -0.095282 | -0.16405 | -0.5 | -0.8 | 5.1112
4690 | 370 | 12.6757 | 0 | 0 | 0 | 318.4207 | 96.8 | 15.92 | 22.61 |  | 2.5397 | -0.16405 | -0.13757 | -0.8 | -0.9 | 5.7824
4750 | 430 | 11.0465 | 0 | 0 | 0 | 315.4602 | 95.9 | 15.02 | 22.29 |  | 2.4021 | -0.13757 | -0.11807 | -0.9 | -0.6 | 5.7563 | -0.31248 | -0.22271 | -1.9 | -1.8 | 7.2491 | 6.0724
4810 | 490 | 9.8163 | 0 | 0 | 0 | 313.4865 | 95.3 | 14.42 | 22.21 |  | 2.284 | -0.11807 | -0.10312 | -0.6 | -0.7 | 5.9928
4870 | 550 | 8.8545 | 0 | 0 | 0 | 311.1839 | 94.6 | 13.72 | 22 |  | 2.1809 | -0.10312 | -0.091296 | -0.7 | -0.6 | 6.6737
4930 | 610 | 8.082 | 0 | 0 | 0 | 309.2102 | 94 | 13.12 | 21.83 |  | 2.0896 | -0.091296 | -0.081722 | -0.6 | -0.6 | 6.9783 | -0.22271 | -0.17064 | -1.8 | -1.7 | 9.1466 | 4.3467
4990 | 670 | 7.4478 | 0 | 0 | 0 | 307.2365 | 93.4 | 12.52 | 21.68 |  | 2.0079 | -0.081722 | -0.073814 | -0.6 | -0.6 | 7.7552
5050 | 730 | 6.9178 | 0 | 0 | 0 | 305.2628 | 92.8 | 11.92 | 21.52 |  | 1.9341 | -0.073814 | -0.067177 | -0.6 | -0.6 | 8.5489
5110 | 790 | 6.4684 | 0 | 0 | 0 | 303.2891 | 92.2 | 11.32 | 21.28 |  | 1.8669 | -0.067177 | -0.06153 | -0.6 | -0.6 | 9.3595 | -0.17064 | -0.13676 | -1.7 | -1.4 | 10.1147 | 7.6077
5170 | 850 | 6.0824 | 0 | 0 | 0 | 301.3154 | 91.6 | 10.72 | 21.08 |  | 1.8054 | -0.06153 | -0.05667 | -0.6 | -0.5 | 9.2681
5230 | 910 | 5.7473 | 0 | 0 | 0 | 299.6707 | 91.1 | 10.22 | 20.95 |  | 1.7487 | -0.05667 | -0.052445 | -0.5 | -0.6 | 10.1825
5290 | 970 | 5.4536 | 0 | 0 | 0 | 297.697 | 90.5 | 9.62 | 20.73 |  | 1.6963 | -0.052445 | -0.04874 | -0.6 | -0.5 | 10.828 | -0.13676 | -0.11304 | -1.4 | -1.4 | 11.4129 | 24.3705
5350 | 1030 | 5.1942 | 0 | 0 | 0 | 296.0523 | 90 | 9.12 | 20.56 |  | 1.6475 | -0.04874 | -0.045466 | -0.5 | -0.5 | 10.6407
5410 | 1090 | 4.9633 | 0 | 0 | 0 | 294.4076 | 89.5 | 8.62 | 20.48 |  | 1.6021 | -0.045466 | -0.042555 | -0.5 | -0.4 | 10.172
5470 | 1150 | 4.7565 | 0 | 0 | 0 | 293.0918 | 89.1 | 8.22 | 20.48 |  | 1.5595 | -0.042555 | -0.039949 | -0.4 | -0.5 | 11.007 | -0.11304 | -0.095569 | -1.4 | -1.6 | 14.7458 | 13.24
5530 | 1210 | 4.5702 | 0 | 0 | 0 | 291.447 | 88.6 | 7.72 | 20.35 |  | 1.5196 | -0.039949 | -0.037605 | -0.5 | -0.5 | 12.9178
5590 | 1270 | 4.4016 | 0 | 0 | 0 | 289.8023 | 88.1 | 7.22 | 20.19 |  | 1.482 | -0.037605 | -0.035486 | -0.5 | -0.4 | 12.2547
5650 | 1330 | 4.2481 | 0 | 0 | 0 | 288.4865 | 87.7 | 6.82 | 20.11 |  | 1.4465 | -0.035486 | -0.033561 | -0.4 | -0.4 | 11.6043 | -0.095569 | -0.082211 | -1.6 | -1.3 | 16.2425 | 0.66745
5710 | 1390 | 4.1079 | 0 | 0 | 0 | 287.1707 | 87.3 | 6.42 | 20.05 |  | 1.4129 | -0.033561 | -0.031807 | -0.4 | -0.7 | 17.0986
5770 | 1450 | 3.9793 | 0 | 0 | 0 | 284.8681 | 86.6 | 5.72 | 19.66 |  | 1.3811 | -0.031807 | -0.030201 | -0.7 | -0.5 | 19.2112
5830 | 1510 | 3.8609 | 0 | 0 | 0 | 283.2234 | 86.1 | 5.22 | 19.47 |  | 1.3509 | -0.030201 | -0.028727 | -0.5 | -0.4 | 15.207 | -0.082211 | -0.0717 | -1.3 | -1.2 | 16.3063 | 9.4886
5890 | 1570 | 3.7516 | 0 | 0 | 0 | 281.9076 | 85.7 | 4.82 | 19.38 |  | 1.3222 | -0.028727 | -0.027369 | -0.4 | -0.5 | 16.149
5950 | 1630 | 3.6503 | 0 | 0 | 0 | 280.2628 | 85.2 | 4.32 | 19.16 |  | 1.2948 | -0.027369 | -0.026115 | -0.5 | -0.4 | 16.7582
6010 | 1690 | 3.5562 | 0 | 0 | 0 | 278.9471 | 84.8 | 3.92 | 19.01 |  | 1.2687 | -0.026115 | -0.024953 | -0.4 | -0.4 | 15.6815 | -0.0717 | -0.063237 | -1.2 | -1.1 | 17.0863 | 7.0207
6070 | 1750 | 3.4686 | 0 | 0 | 0 | 277.6313 | 84.4 | 3.52 | 18.88 |  | 1.2437 | -0.024953 | -0.023875 | -0.4 | -0.4 | 16.3999
6130 | 1810 | 3.3867 | 0 | 0 | 0 | 276.3155 | 84 | 3.12 | 18.73 |  | 1.2199 | -0.023875 | -0.022871 | -0.4 | -0.4 | 17.1296
6190 | 1870 | 3.3102 | 0 | 0 | 0 | 274.9997 | 83.6 | 2.72 | 18.59 |  | 1.197 | -0.022871 | -0.021935 | -0.4 | -0.4 | 17.8701 | -0.063237 | -0.056296 | -1.1 | -1 | 17.5897 | 3.1875
6250 | 1930 | 3.2383 | 0 | 0 | 0 | 273.6839 | 83.2 | 2.32 | 18.46 |  | 1.1751 | -0.021935 | -0.02106 | -0.4 | -0.3 | 16.1995
6310 | 1990 | 3.1709 | 0 | 0 | 0 | 272.6971 | 82.9 | 2.02 | 18.39 |  | 1.154 | -0.02106 | -0.020241 | -0.3 | -0.4 | 17.0578
6370 | 2050 | 3.1073 | 0 | 0 | 0 | 271.3813 | 82.5 | 1.62 | 18.25 |  | 1.1338 | -0.020241 | -0.019473 | -0.4 | -0.4 | 20.159 | -0.056296 | -0.050515 | -1 | -0.9 | 17.7913 | 38.6701
6430 | 2110 | 3.0474 | 0 | 0 | 0 | 270.0655 | 82.1 | 1.22 | 18.1 |  | 1.1143 | -0.019473 | -0.018751 | -0.4 | -0.3 | 18.2272
6490 | 2170 | 2.9908 | 0 | 0 | 0 | 269.0786 | 81.8 | 0.92 | 18.01 |  | 1.0955 | -0.018751 | -0.018072 | -0.3 | -0.3 | 16.3052
6550 | 2230 | 2.9372 | 0 | 0 | 0 | 268.0918 | 81.5 | 0.62 | 17.98 |  | 1.0775 | -0.018072 | -0.017432 | -0.3 | -0.4 | 19.8308 | -0.050515 | -0.045637 | -0.9 | -1 | 19.9683 | 11.2803
6610 | 2290 | 2.8865 | 0 | 0 | 0 | 266.776 | 81.1 | 0.22 | 17.77 |  | 1.06 | -0.017432 | -0.016827 | -0.4 | -0.3 | 20.3424
6670 | 2350 | 2.8383 | 0 | 0 | 0 | 265.7892 | 80.8 | -0.080001 | 17.65 |  | 1.0432 | -0.016827 | -0.016256 | -0.3 | -0.2 | 15.0179
6730 | 2410 | 2.7925 | 0 | 0 | 0 | 265.1313 | 80.6 | -0.28 | 17.66 |  | 1.0269 | -0.016256 | -0.015716 | -0.2 | -0.4 | 18.9888 | -0.045637 | -0.041474 | -1 | -0.8 | 20.5381 | -6.4518
6790 | 2470 | 2.749 | 0 | 0 | 0 | 263.8155 | 80.2 | -0.68 | 17.45 |  | 1.0112 | -0.015716 | -0.015203 | -0.4 | -0.3 | 22.5449
6850 | 2530 | 2.7075 | 0 | 0 | 0 | 262.8287 | 79.9 | -0.98 | 17.37 |  | 0.99603 | -0.015203 | -0.014718 | -0.3 | -0.3 | 20.0634
6910 | 2590 | 2.668 | 0 | 0 | 0 | 261.8418 | 79.6 | -1.28 | 17.36 |  | 0.98131 | -0.014718 | -0.014256 | -0.3 | -0.2 | 17.1558 | -0.041474 | -0.037887 | -0.8 | -0.8 | 20.2436 | 8.6592
6970 | 2650 | 2.6302 | 0 | 0 | 0 | 261.1839 | 79.4 | -1.48 | 17.39 |  | 0.96706 | -0.014256 | -0.013818 | -0.2 | -0.3 | 17.9303
7030 | 2710 | 2.5941 | 0 | 0 | 0 | 260.1971 | 79.1 | -1.78 | 17.3 |  | 0.95324 | -0.013818 | -0.0134 | -0.3 | -0.3 | 22.055
7090 | 2770 | 2.5596 | 0 | 0 | 0 | 259.2102 | 78.8 | -2.08 | 17.22 |  | 0.93984 | -0.0134 | -0.013002 | -0.3 | -0.3 | 22.7354 | -0.037887 | -0.03477 | -0.8 | -0.7 | 20.6028 | 11.1321
7150 | 2830 | 2.5265 | 0 | 0 | 0 | 258.2234 | 78.5 | -2.38 | 17.12 |  | 0.92684 | -0.013002 | -0.012623 | -0.3 | -0.2 | 19.4048
7210 | 2890 | 2.4948 | 0 | 0 | 0 | 257.5655 | 78.3 | -2.58 | 17.12 |  | 0.91421 | -0.012623 | -0.012261 | -0.2 | -0.3 | 20.2182
7270 | 2950 | 2.4644 | 0 | 0 | 0 | 256.5787 | 78 | -2.88 | 17.07 |  | 0.90195 | -0.012261 | -0.011916 | -0.3 | -0.2 | 20.571 | -0.03477 | -0.032041 | -0.7 | -0.7 | 21.0245 | 50.1337
7330 | 3010 | 2.4352 | 0 | 0 | 0 | 255.9208 | 77.8 | -3.08 | 16.97 |  | 0.89004 | -0.011916 | -0.011585 | -0.2 | -0.2 | 17.0274
7390 | 3070 | 2.4072 | 0 | 0 | 0 | 255.2629 | 77.6 | -3.28 | 16.95 |  | 0.87845 | -0.011585 | -0.011269 | -0.2 | -0.3 | 22.0071
7450 | 3130 | 2.3802 | 0 | 0 | 0 | 254.276 | 77.3 | -3.58 | 16.82 |  | 0.86718 | -0.011269 | -0.010966 | -0.3 | -0.2 | 22.3723 | -0.032041 | -0.029636 | -0.7 | -0.7 | 22.7677 | -2.6255
7510 | 3190 | 2.3542 | 0 | 0 | 0 | 253.6181 | 77.1 | -3.78 | 16.78 |  | 0.85621 | -0.010966 | -0.010676 | -0.2 | -0.3 | 23.2343
7570 | 3250 | 2.3292 | 0 | 0 | 0 | 252.6313 | 76.8 | -4.08 | 16.62 |  | 0.84554 | -0.010676 | -0.010398 | -0.3 | -0.2 | 23.6079
7630 | 3310 | 2.3051 | 0 | 0 | 0 | 251.9734 | 76.6 | -4.28 | 16.57 |  | 0.83514 | -0.010398 | -0.010132 | -0.2 | -0.3 | 24.4894 | -0.029636 | -0.027504 | -0.7 | -0.6 | 22.6836 | -69.2605
7690 | 3370 | 2.2819 | 0 | 0 | 0 | 250.9866 | 76.3 | -4.58 | 16.43 |  | 0.82501 | -0.010132 | -0.0098755 | -0.3 | -0.2 | 24.8713
7750 | 3430 | 2.2595 | 0 | 0 | 0 | 250.3287 | 76.1 | -4.78 | 16.4 |  | 0.81513 | -0.0098755 | -0.0096294 | -0.2 | -0.2 | 20.5142
7810 | 3490 | 2.2378 | 0 | 0 | 0 | 249.6708 | 75.9 | -4.98 | 16.36 |  | 0.8055 | -0.0096294 | -0.0093928 | -0.2 | -0.2 | 21.0345 | -0.027504 | -0.025603 | -0.6 | -0.5 | 20.6309 | -73.1103
7870 | 3550 | 2.2169 | 0 | 0 | 0 | 249.0129 | 75.7 | -5.18 | 16.32 |  | 0.79611 | -0.0093928 | -0.0091652 | -0.2 | -0.2 | 21.5607
7930 | 3610 | 2.1967 | 0 | 0 | 0 | 248.355 | 75.5 | -5.38 | 16.3 |  | 0.78695 | -0.0091652 | -0.0089462 | -0.2 | -0.2 | 22.0921
7990 | 3670 | 2.1771 | 0 | 0 | 0 | 247.6971 | 75.3 | -5.58 | 16.26 |  | 0.778 | -0.0089462 | -0.0087352 | -0.2 | -0.2 | 22.6292 | -0.025603 | -0.7524 | -0.5 | 6.08 | 18.6201 | #DIV/0!
8050 | 3730 | 2.1582 | 0 | 0 | 0 | 247.0392 | 75.1 | -5.78 | 16.21 |  | 0.76926 | -0.0087352 | -0.008532 | -0.2 | -0.099998 | 17.2424
8110 | 3790 | 2.1398 | 0 | 0 | 0 | 246.7103 | 75 | -5.88 | 16.25 |  | 0.76073 | -0.008532 | -0.0083361 | -0.099998 | -0.2 | 17.9275
8170 | 3850 | 2.1221 | 0 | 0 | 0 | 246.0524 | 74.8 | -6.08 | 16.18 |  | 0.7524 | -0.0083361 | -0.0081471 | -0.2 | -0.2 | 24.2736 | -0.7524 | 0 | 6.08 | 0 | #DIV/0! | #DIV/0!
8230 | 3910 | 2.1049 | 0 | 0 | 0 | 245.3945 | 74.6 | -6.28 | 16.12 |  | 0.74425 | -0.0081471 | -0.0079648 | -0.2 | -0.2 | 24.8326
8290 | 3970 | 2.0882 | 0 | 0 | 0 | 244.7366 | 74.4 | -6.48 | 16.04 |  | 0.73628 | -0.0079648 | -0.73628 | -0.2 | 6.48 | 24.7473
d2s/d(ln(t))2 ≈ 0.5 m

## Hydraulic Paramaters
Aquifer Hydraulic Paramaters | [12 empty] | Well Hydraulic Paramaters
| Theis Curve-Matching Method |  |  |  | Cooper-Jacob Straight Line Method |  |  |  | Theis Recovery Method |  |  |  |  | Long Term Yield (100 day method)
|  | Equations |  |  |  | Equations |  |  |  | Equations |  |  |  |  | Equations
| T = ( Q * W (u) ) / ( 4 * pi * s ) |  |  |  | T = ( 2.3 * Q ) / ( 4 * pi * slope ) |  |  |  | T = ( 2.3 * Q ) / ( 4 * pi * slope ) |  |  |  |  | Q100 = SAD*SC = 0.7*Available DD*Q/100 Day DD
Available DD = Well Depth - SWL - Pump Submergence
|  | Variables |  |  |  | Variables |  |  |  | Variables |  |  |  |  | Variables
| Note: Taken from radial flow time segment |  |  |  | Note: Taken from radial flow time segment |  |  |  | Note: Taken from radial flow time segment |  |  |  |  | Q (Discharge Rate) |  | 518.4 | m3/day
[14 empty] | 100 Day DD |  | 56 | m
| Match Point |  |  |  | Slope is for 1 log10 cycle of time |  |  |  | Slope is for 1 log10 cycle of time |  |  |  |  | Well Depth |  | 135.6 | m
| s (Drawdown) |  | 20 | m | Q (Discharge Rate) |  | 518.4 | m3/day | [5 empty] | SWL |  | 80.88 | m
| t (time) |  | N/A | min | slope (ds/dlog(t)) |  | 21 | m | Q (Discharge Rate) |  | 518.4 | m3/day |  | Pump Submergence |  | 3 | m
| W(u) |  | 2 |  | to (Intercept Time) |  | N/A |  | slope (ds/dlog(t/t')) |  | 47.5 | m
| 1/u |  |  |  | r (Radius) |  | N/A |  | to (Intercept Time) |  | N/A
[9 empty] | r (Radius) |  | N/A
| Q ((Discharge Rate) |  | 518.4 | m3/day
| r (Radius) |  | N/A | m
| T (Transmissivity) |  | 4.124 | m2/day | T (Transmissivity) |  | 4.518 | m2/day | T (Transmissivity) |  | 1.998 | m2/day |  | Q100 |  | 335.1456 | m3/day
100 Day Drawdown = 56.0 m
100 Days
ds/d(log(t/t')) = 47.5m
Match Point
ds/d(log(t)) = 21.0 m
Adjusted ds/d(log(t)) = 33.0 m
Adjusted 100 Day Drawdown = 81 m