## Pumped Well Info
WELL, TEST, AQUIFER INFORMATION FOR PUMPING WELL
Well Information |  | Test Information |  | Aquifer Information
Well Name: | Saanich North Well | Date of start of test (yyyy-mm-dd): | 2022-08-23 | Aquifer Number: | 614
Well ID Plate Number: | Unknown | Type of test (step test, constant rate test): | constant rate test | Aquifer Lithology | Granite (Karmutsen Formation)
Well Tag Number: | 53884 | SWL at start of test (m): | 5.34 | Aquifer Type: | Fractured Crystalline Bedrock
Well Location : | Tsartlip First Nation | Reference datum for water level measurements (top of production casing): |  | Depth to upper-most water bearing fracture (m) | 31.08
UTM Zone (easting, northing): |  | Datalogger water level measurements?: | Yes
Well Casing Inside Diameter (mm): | 150 | Was a step-drawdown test performed before the constant rate test? | No
Driller's Well Record (image):

## Pumped Well Data
Pumped Well Data
WTN | 53884 | SWL (m): | 5.34 |  | Average Pumping Rate (m3/day): |  |  | 70.84
Derivative is very noisy due to the amplification of small measuments errors. Derivative will be easier to interpret with a greater L-spacing inverval (L=8 was chosen)
Time since pumping started, t (min) | Time since pumping stopped, t' (min) | t/t' | Pumping rate, Q (USgpm) | Pumping rate, Q (L/s) | Pumping Rate, Q (m3/day) | Water Level (ft) | Water Level (m) | Drawdown or Residual Drawdown (m) | Extended Drawdown (m) | ln(t) | Dt1 | Dt2 | Ds1 | Ds2 | ds/dt | Dt1 | Dt2 | Ds1 | Ds2 | ds/dt (L-Spacing = 8) | d2s/dt2
0 | - | - | 13 | 0.82017 | 70.84 | 17.5205 | 5.34 | 0 | 0 | #NUM! | #NUM! | #NUM! | #REF! | 2.2774 | #REF!
1 | - | - | 13 | 0.82017 | 70.84 | 24.9927 | 7.6174 | 2.2774 | 2.2774 | 0 | #NUM! | 2.3979 | 2.2774 | 4.6961 | #NUM!
11 | - | - | 13 | 0.82017 | 70.84 | 40.4006 | 12.3135 | 6.9735 | 6.9735 | 2.3979 | 2.3979 | 0.64663 | 4.6961 | 1.5581 | 2.3138 | 2.113 | 0.6308 | 5.0283 | 1.9831 | 2.9681
21 | - | - | 13 | 0.82017 | 70.84 | 45.5127 | 13.8716 | 8.5316 | 8.5316 | 3.0445 | 0.64663 | 0.38946 | 1.5581 | 0.9324 | 2.3999
31 | - | - | 13 | 0.82017 | 70.84 | 48.5719 | 14.804 | 9.464 | 9.464 | 3.434 | 0.38946 | 0.27958 | 0.9324 | 0.7045 | 2.4673
41 | - | - | 13 | 0.82017 | 70.84 | 50.8834 | 15.5085 | 10.1685 | 10.1685 | 3.7136 | 0.27958 | 0.21825 | 0.7045 | 0.5291 | 2.4661
51 | - | - | 13 | 0.82017 | 70.84 | 52.6194 | 16.0376 | 10.6976 | 10.6976 | 3.9318 | 0.21825 | 0.17905 | 0.5291 | 0.4149 | 2.3655
61 | - | - | 13 | 0.82017 | 70.84 | 53.9807 | 16.4525 | 11.1125 | 11.1125 | 4.1109 | 0.17905 | 0.15181 | 0.4149 | 0.3388 | 2.271
71 | - | - | 13 | 0.82017 | 70.84 | 55.0923 | 16.7913 | 11.4513 | 11.4513 | 4.2627 | 0.15181 | 0.13177 | 0.3388 | 0.2957 | 2.2384
81 | - | - | 13 | 0.82017 | 70.84 | 56.0624 | 17.087 | 11.747 | 11.747 | 4.3944 | 0.13177 | 0.11641 | 0.2957 | 0.2548 | 2.2147
91 | - | - | 13 | 0.82017 | 70.84 | 56.8984 | 17.3418 | 12.0018 | 12.0018 | 4.5109 | 0.11641 | 0.10426 | 0.2548 | 0.2236 | 2.1655 | 0.6308 | 0.38379 | 1.9831 | 0.9661 | 2.7543
101 | - | - | 13 | 0.82017 | 70.84 | 57.6321 | 17.5654 | 12.2254 | 12.2254 | 4.6151 | 0.10426 | 0.09441 | 0.2236 | 0.2084 | 2.1776
111 | - | - | 13 | 0.82017 | 70.84 | 58.3158 | 17.7738 | 12.4338 | 12.4338 | 4.7095 | 0.09441 | 0.08626 | 0.2084 | 0.1966 | 2.2449
121 | - | - | 13 | 0.82017 | 70.84 | 58.9609 | 17.9704 | 12.6304 | 12.6304 | 4.7958 | 0.08626 | 0.079407 | 0.1966 | 0.1892 | 2.333
131 | - | - | 13 | 0.82017 | 70.84 | 59.5816 | 18.1596 | 12.8196 | 12.8196 | 4.8752 | 0.079407 | 0.073563 | 0.1892 | 0.5537 | 5.0531
141 | - | - | 13 | 0.82017 | 70.84 | 61.3983 | 18.7133 | 13.3733 | 13.3733 | 4.9488 | 0.073563 | 0.06852 | 0.5537 | 0.2498 | 5.5174
151 | - | - | 13 | 0.82017 | 70.84 | 62.2179 | 18.9631 | 13.6231 | 13.6231 | 5.0173 | 0.06852 | 0.064125 | 0.2498 | 0.1854 | 3.256
161 | - | - | 13 | 0.82017 | 70.84 | 62.8262 | 19.1485 | 13.8085 | 13.8085 | 5.0814 | 0.064125 | 0.060259 | 0.1854 | 0.1764 | 2.9099
171 | - | - | 13 | 0.82017 | 70.84 | 63.405 | 19.3249 | 13.9849 | 13.9849 | 5.1417 | 0.060259 | 0.056833 | 0.1764 | 0.1441 | 2.7257 | 0.38379 | 0.27667 | 0.9661 | 0.6477 | 2.4149
181 | - | - | 13 | 0.82017 | 70.84 | 63.8778 | 19.469 | 14.129 | 14.129 | 5.1985 | 0.056833 | 0.053776 | 0.1441 | 0.1328 | 2.5016
191 | - | - | 13 | 0.82017 | 70.84 | 64.3135 | 19.6018 | 14.2618 | 14.2618 | 5.2523 | 0.053776 | 0.051031 | 0.1328 | 0.1351 | 2.5608
201 | - | - | 13 | 0.82017 | 70.84 | 64.7568 | 19.7369 | 14.3969 | 14.3969 | 5.3033 | 0.051031 | 0.048553 | 0.1351 | 0.1326 | 2.6902
211 | - | - | 13 | 0.82017 | 70.84 | 65.1918 | 19.8695 | 14.5295 | 14.5295 | 5.3519 | 0.048553 | 0.046305 | 0.1326 | 0.1144 | 2.5977
221 | - | - | 13 | 0.82017 | 70.84 | 65.5672 | 19.9839 | 14.6439 | 14.6439 | 5.3982 | 0.046305 | 0.044255 | 0.1144 | 0.1153 | 2.5395
231 | - | - | 13 | 0.82017 | 70.84 | 65.9455 | 20.0992 | 14.7592 | 14.7592 | 5.4424 | 0.044255 | 0.042379 | 0.1153 | 0.0983 | 2.4593
241 | - | - | 13 | 0.82017 | 70.84 | 66.268 | 20.1975 | 14.8575 | 14.8575 | 5.4848 | 0.042379 | 0.040656 | 0.0983 | 0.0935 | 2.3095
251 | - | - | 13 | 0.82017 | 70.84 | 66.5748 | 20.291 | 14.951 | 14.951 | 5.5255 | 0.040656 | 0.039067 | 0.0935 | 0.0953 | 2.371 | 0.27667 | 0.21647 | 0.6477 | 0.4307 | 2.1439
261 | - | - | 13 | 0.82017 | 70.84 | 66.8875 | 20.3863 | 15.0463 | 15.0463 | 5.5645 | 0.039067 | 0.037598 | 0.0953 | 0.0917 | 2.4391
271 | - | - | 13 | 0.82017 | 70.84 | 67.1883 | 20.478 | 15.138 | 15.138 | 5.6021 | 0.037598 | 0.036236 | 0.0917 | 0.0886 | 2.4421
281 | - | - | 13 | 0.82017 | 70.84 | 67.479 | 20.5666 | 15.2266 | 15.2266 | 5.6384 | 0.036236 | 0.034969 | 0.0886 | 0.0809 | 2.3781
291 | - | - | 13 | 0.82017 | 70.84 | 67.7444 | 20.6475 | 15.3075 | 15.3075 | 5.6733 | 0.034969 | 0.033787 | 0.0809 | 0.0664 | 2.1364
301 | - | - | 13 | 0.82017 | 70.84 | 67.9623 | 20.7139 | 15.3739 | 15.3739 | 5.7071 | 0.033787 | 0.032683 | 0.0664 | 0.0805 | 2.2183
311 | - | - | 13 | 0.82017 | 70.84 | 68.2264 | 20.7944 | 15.4544 | 15.4544 | 5.7398 | 0.032683 | 0.031648 | 0.0805 | 0.0781 | 2.4655
321 | - | - | 13 | 0.82017 | 70.84 | 68.4827 | 20.8725 | 15.5325 | 15.5325 | 5.7714 | 0.031648 | 0.030677 | 0.0781 | 0.0662 | 2.3104
331 | - | - | 13 | 0.82017 | 70.84 | 68.6999 | 20.9387 | 15.5987 | 15.5987 | 5.8021 | 0.030677 | 0.029764 | 0.0662 | 0.0372 | 1.697 | 0.21647 | 0.17785 | 0.4307 | 0.3536 | 1.9888
341 | - | - | 13 | 0.82017 | 70.84 | 68.8219 | 20.9759 | 15.6359 | 15.6359 | 5.8319 | 0.029764 | 0.028904 | 0.0372 | 0.0829 | 2.0709
351 | - | - | 13 | 0.82017 | 70.84 | 69.0939 | 21.0588 | 15.7188 | 15.7188 | 5.8608 | 0.028904 | 0.028092 | 0.0829 | 0.0497 | 2.3108
361 | - | - | 13 | 0.82017 | 70.84 | 69.257 | 21.1085 | 15.7685 | 15.7685 | 5.8889 | 0.028092 | 0.027324 | 0.0497 | 0.0628 | 2.0374
371 | - | - | 13 | 0.82017 | 70.84 | 69.463 | 21.1713 | 15.8313 | 15.8313 | 5.9162 | 0.027324 | 0.026597 | 0.0628 | 0.0469 | 2.0272
381 | - | - | 13 | 0.82017 | 70.84 | 69.6169 | 21.2182 | 15.8782 | 15.8782 | 5.9428 | 0.026597 | 0.025908 | 0.0469 | 0.0558 | 1.9611
391 | - | - | 13 | 0.82017 | 70.84 | 69.8 | 21.274 | 15.934 | 15.934 | 5.9687 | 0.025908 | 0.025254 | 0.0558 | 0.0393 | 1.8512
401 | - | - | 13 | 0.82017 | 70.84 | 69.9289 | 21.3133 | 15.9733 | 15.9733 | 5.994 | 0.025254 | 0.024632 | 0.0393 | 0.0561 | 1.9214
411 | - | - | 13 | 0.82017 | 70.84 | 70.113 | 21.3694 | 16.0294 | 16.0294 | 6.0186 | 0.024632 | 0.02404 | 0.0561 | 0.0474 | 2.1228 | 0.17785 | 0.15095 | 0.3536 | 0.2769 | 1.905
421 | - | - | 13 | 0.82017 | 70.84 | 70.2685 | 21.4168 | 16.0768 | 16.0768 | 6.0426 | 0.02404 | 0.023475 | 0.0474 | 0.0518 | 2.0906
431 | - | - | 13 | 0.82017 | 70.84 | 70.4385 | 21.4686 | 16.1286 | 16.1286 | 6.0661 | 0.023475 | 0.022937 | 0.0518 | 0.0408 | 1.9902
441 | - | - | 13 | 0.82017 | 70.84 | 70.5723 | 21.5094 | 16.1694 | 16.1694 | 6.089 | 0.022937 | 0.022422 | 0.0408 | 0.04 | 1.7814
451 | - | - | 13 | 0.82017 | 70.84 | 70.7036 | 21.5494 | 16.2094 | 16.2094 | 6.1115 | 0.022422 | 0.021931 | 0.04 | 0.0458 | 1.9378
461 | - | - | 13 | 0.82017 | 70.84 | 70.8539 | 21.5952 | 16.2552 | 16.2552 | 6.1334 | 0.021931 | 0.02146 | 0.0458 | 0.0395 | 1.9632
471 | - | - | 13 | 0.82017 | 70.84 | 70.9835 | 21.6347 | 16.2947 | 16.2947 | 6.1549 | 0.02146 | 0.021009 | 0.0395 | 0.0482 | 2.0698
481 | - | - | 13 | 0.82017 | 70.84 | 71.1416 | 21.6829 | 16.3429 | 16.3429 | 6.1759 | 0.021009 | 0.020577 | 0.0482 | 0.0401 | 2.1197
491 | - | - | 13 | 0.82017 | 70.84 | 71.2732 | 21.723 | 16.383 | 16.383 | 6.1964 | 0.020577 | 0.020162 | 0.0401 | 0.0331 | 1.7937 | 0.15095 | 0.13112 | 0.2769 | 0.2516 | 1.8796
501 | - | - | 13 | 0.82017 | 70.84 | 71.3818 | 21.7561 | 16.4161 | 16.4161 | 6.2166 | 0.020162 | 0.019763 | 0.0331 | 0.037 | 1.7581
511 | - | - | 13 | 0.82017 | 70.84 | 71.5032 | 21.7931 | 16.4531 | 16.4531 | 6.2364 | 0.019763 | 0.01938 | 0.037 | 0.0338 | 1.8075
521 | - | - | 13 | 0.82017 | 70.84 | 71.6141 | 21.8269 | 16.4869 | 16.4869 | 6.2558 | 0.01938 | 0.019012 | 0.0338 | 0.0325 | 1.7266
531 | - | - | 13 | 0.82017 | 70.84 | 71.7207 | 21.8594 | 16.5194 | 16.5194 | 6.2748 | 0.019012 | 0.018657 | 0.0325 | 0.0511 | 2.229
541 | - | - | 13 | 0.82017 | 70.84 | 71.8884 | 21.9105 | 16.5705 | 16.5705 | 6.2934 | 0.018657 | 0.018316 | 0.0511 | 0.0283 | 2.1365
551 | - | - | 13 | 0.82017 | 70.84 | 71.9812 | 21.9388 | 16.5988 | 16.5988 | 6.3117 | 0.018316 | 0.017986 | 0.0283 | 0.0239 | 1.436
561 | - | - | 13 | 0.82017 | 70.84 | 72.0596 | 21.9627 | 16.6227 | 16.6227 | 6.3297 | 0.017986 | 0.017668 | 0.0239 | 0.0372 | 1.7206
571 | - | - | 13 | 0.82017 | 70.84 | 72.1817 | 21.9999 | 16.6599 | 16.6599 | 6.3474 | 0.017668 | 0.017362 | 0.0372 | 0.0357 | 2.0807 | 0.13112 | 0.1159 | 0.2516 | 0.2309 | 1.9578
581 | - | - | 13 | 0.82017 | 70.84 | 72.2988 | 22.0356 | 16.6956 | 16.6956 | 6.3648 | 0.017362 | 0.017065 | 0.0357 | 0.0296 | 1.894
591 | - | - | 13 | 0.82017 | 70.84 | 72.3959 | 22.0652 | 16.7252 | 16.7252 | 6.3818 | 0.017065 | 0.016779 | 0.0296 | 0.0246 | 1.5992
601 | - | - | 13 | 0.82017 | 70.84 | 72.4766 | 22.0898 | 16.7498 | 16.7498 | 6.3986 | 0.016779 | 0.016502 | 0.0246 | 0.0465 | 2.1476
611 | - | - | 13 | 0.82017 | 70.84 | 72.6292 | 22.1363 | 16.7963 | 16.7963 | 6.4151 | 0.016502 | 0.016234 | 0.0465 | 0.028 | 2.2668
621 | - | - | 13 | 0.82017 | 70.84 | 72.7211 | 22.1643 | 16.8243 | 16.8243 | 6.4313 | 0.016234 | 0.015975 | 0.028 | 0.0255 | 1.66
631 | - | - | 13 | 0.82017 | 70.84 | 72.8047 | 22.1898 | 16.8498 | 16.8498 | 6.4473 | 0.015975 | 0.015724 | 0.0255 | 0.0302 | 1.7598
641 | - | - | 13 | 0.82017 | 70.84 | 72.9038 | 22.22 | 16.88 | 16.88 | 6.463 | 0.015724 | 0.01548 | 0.0302 | 0.0315 | 1.9782
651 | - | - | 13 | 0.82017 | 70.84 | 73.0072 | 22.2515 | 16.9115 | 16.9115 | 6.4785 | 0.01548 | 0.015244 | 0.0315 | 0.0313 | 2.0441 | 0.1159 | 0.10385 | 0.2309 | 0.2309 | 2.1141
661 | - | - | 13 | 0.82017 | 70.84 | 73.1099 | 22.2828 | 16.9428 | 16.9428 | 6.4938 | 0.015244 | 0.015015 | 0.0313 | 0.0274 | 1.9382
671 | - | - | 13 | 0.82017 | 70.84 | 73.1998 | 22.3102 | 16.9702 | 16.9702 | 6.5088 | 0.015015 | 0.014793 | 0.0274 | 0.0318 | 1.9884
681 | - | - | 13 | 0.82017 | 70.84 | 73.3041 | 22.342 | 17.002 | 17.002 | 6.5236 | 0.014793 | 0.014578 | 0.0318 | 0.0256 | 1.9514
691 | - | - | 13 | 0.82017 | 70.84 | 73.3881 | 22.3676 | 17.0276 | 17.0276 | 6.5381 | 0.014578 | 0.014368 | 0.0256 | 0.0283 | 1.8637
701 | - | - | 13 | 0.82017 | 70.84 | 73.4809 | 22.3959 | 17.0559 | 17.0559 | 6.5525 | 0.014368 | 0.014165 | 0.0283 | 0.0279 | 1.9697
711 | - | - | 13 | 0.82017 | 70.84 | 73.5725 | 22.4238 | 17.0838 | 17.0838 | 6.5667 | 0.014165 | 0.013967 | 0.0279 | 0.0341 | 2.2073
721 | - | - | 13 | 0.82017 | 70.84 | 73.6844 | 22.4579 | 17.1179 | 17.1179 | 6.5806 | 0.013967 | 0.013774 | 0.0341 | 0.0245 | 2.1078
731 | - | - | 13 | 0.82017 | 70.84 | 73.7648 | 22.4824 | 17.1424 | 17.1424 | 6.5944 | 0.013774 | 0.013587 | 0.0245 | 0.0285 | 1.9392 | 0.10385 | 0.094076 | 0.2309 | 0.1558 | 1.9257
741 | - | - | 13 | 0.82017 | 70.84 | 73.8583 | 22.5109 | 17.1709 | 17.1709 | 6.608 | 0.013587 | 0.013405 | 0.0285 | 0.0356 | 2.3785
751 | - | - | 13 | 0.82017 | 70.84 | 73.9751 | 22.5465 | 17.2065 | 17.2065 | 6.6214 | 0.013405 | 0.013228 | 0.0356 | 0.0262 | 2.316
761 | - | - | 13 | 0.82017 | 70.84 | 74.061 | 22.5727 | 17.2327 | 17.2327 | 6.6346 | 0.013228 | 0.013055 | 0.0262 | 0.0291 | 2.1057
771 | - | - | 13 | 0.82017 | 70.84 | 74.1565 | 22.6018 | 17.2618 | 17.2618 | 6.6477 | 0.013055 | 0.012887 | 0.0291 | 0.0273 | 2.1734
781 | - | - | 13 | 0.82017 | 70.84 | 74.2461 | 22.6291 | 17.2891 | 17.2891 | 6.6606 | 0.012887 | 0.012723 | 0.0273 | 0.0293 | 2.2113
791 | - | - | 13 | 0.82017 | 70.84 | 74.3422 | 22.6584 | 17.3184 | 17.3184 | 6.6733 | 0.012723 | 0.012563 | 0.0293 | 0.0333 | 2.4779
801 | - | - | 13 | 0.82017 | 70.84 | 74.4515 | 22.6917 | 17.3517 | 17.3517 | 6.6859 | 0.012563 | 0.012407 | 0.0333 | 0.0216 | 2.193
811 | - | - | 13 | 0.82017 | 70.84 | 74.5223 | 22.7133 | 17.3733 | 17.3733 | 6.6983 | 0.012407 | 0.012255 | 0.0216 | 0.0161 | 1.526 | 0.094076 | 0.085982 | 0.1558 | 0.1398 | 1.6403
821 | - | - | 13 | 0.82017 | 70.84 | 74.5752 | 22.7294 | 17.3894 | 17.3894 | 6.7105 | 0.012255 | 0.012107 | 0.0161 | 0.0044 | 0.8357
831 | - | - | 13 | 0.82017 | 70.84 | 74.5896 | 22.7338 | 17.3938 | 17.3938 | 6.7226 | 0.012107 | 0.011962 | 0.0044 | 0.0234 | 1.1646
841 | - | - | 13 | 0.82017 | 70.84 | 74.6664 | 22.7572 | 17.4172 | 17.4172 | 6.7346 | 0.011962 | 0.01182 | 0.0234 | 0.0197 | 1.8105
851 | - | - | 13 | 0.82017 | 70.84 | 74.731 | 22.7769 | 17.4369 | 17.4369 | 6.7464 | 0.01182 | 0.011682 | 0.0197 | 0.0213 | 1.7454
861 | - | - | 13 | 0.82017 | 70.84 | 74.8009 | 22.7982 | 17.4582 | 17.4582 | 6.7581 | 0.011682 | 0.011547 | 0.0213 | 0.0255 | 2.0169
871 | - | - | 13 | 0.82017 | 70.84 | 74.8846 | 22.8237 | 17.4837 | 17.4837 | 6.7696 | 0.011547 | 0.011416 | 0.0255 | 0.029 | 2.3753
881 | - | - | 13 | 0.82017 | 70.84 | 74.9797 | 22.8527 | 17.5127 | 17.5127 | 6.7811 | 0.011416 | 0.011287 | 0.029 | 0.0164 | 1.9936
891 | - | - | 13 | 0.82017 | 70.84 | 75.0335 | 22.8691 | 17.5291 | 17.5291 | 6.7923 | 0.011287 | 0.011161 | 0.0164 | 0.0291 | 2.0334 | 0.085982 | 0.079171 | 0.1398 | 0.139 | 1.6935
901 | - | - | 13 | 0.82017 | 70.84 | 75.129 | 22.8982 | 17.5582 | 17.5582 | 6.8035 | 0.011161 | 0.011038 | 0.0291 | 0.0141 | 1.9387
911 | - | - | 13 | 0.82017 | 70.84 | 75.1753 | 22.9123 | 17.5723 | 17.5723 | 6.8145 | 0.011038 | 0.010917 | 0.0141 | 0.0298 | 2.0075
921 | - | - | 13 | 0.82017 | 70.84 | 75.273 | 22.9421 | 17.6021 | 17.6021 | 6.8255 | 0.010917 | 0.010799 | 0.0298 | 0.0221 | 2.3862
931 | - | - | 13 | 0.82017 | 70.84 | 75.3455 | 22.9642 | 17.6242 | 17.6242 | 6.8363 | 0.010799 | 0.010684 | 0.0221 | 0.0165 | 1.7941
941 | - | - | 13 | 0.82017 | 70.84 | 75.3997 | 22.9807 | 17.6407 | 17.6407 | 6.8469 | 0.010684 | 0.010571 | 0.0165 | 0.0204 | 1.7381
951 | - | - | 13 | 0.82017 | 70.84 | 75.4666 | 23.0011 | 17.6611 | 17.6611 | 6.8575 | 0.010571 | 0.01046 | 0.0204 | 0.0059 | 1.2433
961 | - | - | 13 | 0.82017 | 70.84 | 75.486 | 23.007 | 17.667 | 17.667 | 6.868 | 0.01046 | 0.010352 | 0.0059 | 0.0019 | 0.3728
971 | - | - | 13 | 0.82017 | 70.84 | 75.4922 | 23.0089 | 17.6689 | 17.6689 | 6.8783 | 0.010352 | 0.010246 | 0.0019 | 0.0232 | 1.2293 | 0.079171 | 0.07336 | 0.139 | 0.1333 | 1.7875
981 | - | - | 13 | 0.82017 | 70.84 | 75.5683 | 23.0321 | 17.6921 | 17.6921 | 6.8886 | 0.010246 | 0.010142 | 0.0232 | 0.0149 | 1.8647
991 | - | - | 13 | 0.82017 | 70.84 | 75.6172 | 23.047 | 17.707 | 17.707 | 6.8987 | 0.010142 | 0.01004 | 0.0149 | 0.0224 | 1.852
1001 | - | - | 13 | 0.82017 | 70.84 | 75.6907 | 23.0694 | 17.7294 | 17.7294 | 6.9088 | 0.01004 | 0.0099404 | 0.0224 | 0.0208 | 2.1614
1011 | - | - | 13 | 0.82017 | 70.84 | 75.7589 | 23.0902 | 17.7502 | 17.7502 | 6.9187 | 0.0099404 | 0.0098426 | 0.0208 | 0.0139 | 1.7507
1021 | - | - | 13 | 0.82017 | 70.84 | 75.8046 | 23.1041 | 17.7641 | 17.7641 | 6.9285 | 0.0098426 | 0.0097467 | 0.0139 | 0.0148 | 1.4656
1031 | - | - | 13 | 0.82017 | 70.84 | 75.8531 | 23.1189 | 17.7789 | 17.7789 | 6.9383 | 0.0097467 | 0.0096526 | 0.0148 | 0.0128 | 1.4218
1041 | - | - | 13 | 0.82017 | 70.84 | 75.8951 | 23.1317 | 17.7917 | 17.7917 | 6.9479 | 0.0096526 | 0.0095603 | 0.0128 | 0.0162 | 1.5112
1051 | - | - | 13 | 0.82017 | 70.84 | 75.9483 | 23.1479 | 17.8079 | 17.8079 | 6.9575 | 0.0095603 | 0.0094698 | 0.0162 | 0.0247 | 2.1536 | 0.07336 | 0.068344 | 0.1333 | 0.1317 | 1.874
1061 | - | - | 13 | 0.82017 | 70.84 | 76.0293 | 23.1726 | 17.8326 | 17.8326 | 6.967 | 0.0094698 | 0.0093809 | 0.0247 | 0.0179 | 2.2566
1071 | - | - | 13 | 0.82017 | 70.84 | 76.088 | 23.1905 | 17.8505 | 17.8505 | 6.9763 | 0.0093809 | 0.0092937 | 0.0179 | 0.0187 | 1.9604
1081 | - | - | 13 | 0.82017 | 70.84 | 76.1494 | 23.2092 | 17.8692 | 17.8692 | 6.9856 | 0.0092937 | 0.0092082 | 0.0187 | 0.0138 | 1.7542
1091 | - | - | 13 | 0.82017 | 70.84 | 76.1947 | 23.223 | 17.883 | 17.883 | 6.9948 | 0.0092082 | 0.0091242 | 0.0138 | 0.0103 | 1.3129
1101 | - | - | 13 | 0.82017 | 70.84 | 76.2285 | 23.2333 | 17.8933 | 17.8933 | 7.004 | 0.0091242 | 0.0090417 | 0.0103 | 0.0192 | 1.6284
1111 | - | - | 13 | 0.82017 | 70.84 | 76.2915 | 23.2525 | 17.9125 | 17.9125 | 7.013 | 0.0090417 | 0.0089606 | 0.0192 | 0.0106 | 1.6511
1121 | - | - | 13 | 0.82017 | 70.84 | 76.3262 | 23.2631 | 17.9231 | 17.9231 | 7.022 | 0.0089606 | 0.0088811 | 0.0106 | 0.0181 | 1.6124
1131 | - | - | 13 | 0.82017 | 70.84 | 76.3856 | 23.2812 | 17.9412 | 17.9412 | 7.0309 | 0.0088811 | 0.0088029 | 0.0181 | 0.0291 | 2.6747 | 0.068344 | 0.063971 | 0.1317 | 0.1069 | 1.7948
1141 | - | - | 13 | 0.82017 | 70.84 | 76.4811 | 23.3103 | 17.9703 | 17.9703 | 7.0397 | 0.0088029 | 0.0087261 | 0.0291 | 0.011 | 2.2787
1151 | - | - | 13 | 0.82017 | 70.84 | 76.5172 | 23.3213 | 17.9813 | 17.9813 | 7.0484 | 0.0087261 | 0.0086506 | 0.011 | 0.0154 | 1.5215
1161 | - | - | 13 | 0.82017 | 70.84 | 76.5677 | 23.3367 | 17.9967 | 17.9967 | 7.057 | 0.0086506 | 0.0085764 | 0.0154 | 0.0156 | 1.7997
1171 | - | - | 13 | 0.82017 | 70.84 | 76.6189 | 23.3523 | 18.0123 | 18.0123 | 7.0656 | 0.0085764 | 0.0085035 | 0.0156 | 0.0234 | 2.2874
1181 | - | - | 13 | 0.82017 | 70.84 | 76.6957 | 23.3757 | 18.0357 | 18.0357 | 7.0741 | 0.0085035 | 0.0084318 | 0.0234 | 0.0171 | 2.3884
1191 | - | - | 13 | 0.82017 | 70.84 | 76.7518 | 23.3928 | 18.0528 | 18.0528 | 7.0825 | 0.0084318 | 0.0083613 | 0.0171 | 0.0046 | 1.286
1201 | - | - | 13 | 0.82017 | 70.84 | 76.7669 | 23.3974 | 18.0574 | 18.0574 | 7.0909 | 0.0083613 | 0.0082919 | 0.0046 | 0.0155 | 1.2125
1211 | - | - | 13 | 0.82017 | 70.84 | 76.8177 | 23.4129 | 18.0729 | 18.0729 | 7.0992 | 0.0082919 | 0.0082237 | 0.0155 | 0.0166 | 1.9442 | 0.063971 | 0.060123 | 0.1069 | 0.1219 | 1.8548
1221 | - | - | 13 | 0.82017 | 70.84 | 76.8722 | 23.4295 | 18.0895 | 18.0895 | 7.1074 | 0.0082237 | 0.0081567 | 0.0166 | 0.0071 | 1.4422
1231 | - | - | 13 | 0.82017 | 70.84 | 76.8955 | 23.4366 | 18.0966 | 18.0966 | 7.1156 | 0.0081567 | 0.0080907 | 0.0071 | 0.0152 | 1.3766
1241 | - | - | 13 | 0.82017 | 70.84 | 76.9454 | 23.4518 | 18.1118 | 18.1118 | 7.1237 | 0.0080907 | 0.0080257 | 0.0152 | 0.0174 | 2.024
1251 | - | - | 13 | 0.82017 | 70.84 | 77.0024 | 23.4692 | 18.1292 | 18.1292 | 7.1317 | 0.0080257 | 0.0079618 | 0.0174 | 0.0184 | 2.2398
1261 | - | - | 13 | 0.82017 | 70.84 | 77.0628 | 23.4876 | 18.1476 | 18.1476 | 7.1397 | 0.0079618 | 0.0078989 | 0.0184 | 0.0048 | 1.456
1271 | - | - | 13 | 0.82017 | 70.84 | 77.0786 | 23.4924 | 18.1524 | 18.1524 | 7.1476 | 0.0078989 | 0.007837 | 0.0048 | 0.0138 | 1.1865
1281 | - | - | 13 | 0.82017 | 70.84 | 77.1238 | 23.5062 | 18.1662 | 18.1662 | 7.1554 | 0.007837 | 0.0077761 | 0.0138 | 0.0136 | 1.7549
1291 | - | - | 13 | 0.82017 | 70.84 | 77.1685 | 23.5198 | 18.1798 | 18.1798 | 7.1632 | 0.0077761 | 0.0077161 | 0.0136 | 0.007 | 1.3264 | 0.060123 | 0.056713 | 0.1219 | 0.0942 | 1.8389
1301 | - | - | 13 | 0.82017 | 70.84 | 77.1914 | 23.5268 | 18.1868 | 18.1868 | 7.1709 | 0.0077161 | 0.007657 | 0.007 | 0.0105 | 1.1401
1311 | - | - | 13 | 0.82017 | 70.84 | 77.2259 | 23.5373 | 18.1973 | 18.1973 | 7.1785 | 0.007657 | 0.0075988 | 0.0105 | 0.0155 | 1.7068
1321 | - | - | 13 | 0.82017 | 70.84 | 77.2767 | 23.5528 | 18.2128 | 18.2128 | 7.1861 | 0.0075988 | 0.0075415 | 0.0155 | 0.0042 | 1.2955
1331 | - | - | 13 | 0.82017 | 70.84 | 77.2905 | 23.557 | 18.217 | 18.217 | 7.1937 | 0.0075415 | 0.0074851 | 0.0042 | 0.0224 | 1.7793
1341 | - | - | 13 | 0.82017 | 70.84 | 77.364 | 23.5794 | 18.2394 | 18.2394 | 7.2012 | 0.0074851 | 0.0074295 | 0.0224 | 0.0076 | 2.0041
1351 | - | - | 13 | 0.82017 | 70.84 | 77.3889 | 23.587 | 18.247 | 18.247 | 7.2086 | 0.0074295 | 0.0073747 | 0.0076 | 0.0308 | 2.6055
1361 | - | - | 13 | 0.82017 | 70.84 | 77.49 | 23.6178 | 18.2778 | 18.2778 | 7.216 | 0.0073747 | 0.0073207 | 0.0308 | 0.0239 | 3.7189
1371 | - | - | 13 | 0.82017 | 70.84 | 77.5684 | 23.6417 | 18.3017 | 18.3017 | 7.2233 | 0.0073207 | 0.0072675 | 0.0239 | 0.0145 | 2.6276 | 0.056713 | 0.053668 | 0.0942 | 0.107 | 1.832
1381 | - | - | 13 | 0.82017 | 70.84 | 77.616 | 23.6562 | 18.3162 | 18.3162 | 7.2306 | 0.0072675 | 0.007215 | 0.0145 | 0.0069 | 1.4739
1391 | - | - | 13 | 0.82017 | 70.84 | 77.6386 | 23.6631 | 18.3231 | 18.3231 | 7.2378 | 0.007215 | 0.0071634 | 0.0069 | 0.0174 | 1.6953
1401 | - | - | 13 | 0.82017 | 70.84 | 77.6957 | 23.6805 | 18.3405 | 18.3405 | 7.2449 | 0.0071634 | 0.0071124 | 0.0174 | 0.0025 | 1.3866
1411 | - | - | 13 | 0.82017 | 70.84 | 77.7039 | 23.683 | 18.343 | 18.343 | 7.2521 | 0.0071124 | 0.0070622 | 0.0025 | 0.0082 | 0.75774
1421 | - | - | 13 | 0.82017 | 70.84 | 77.7308 | 23.6912 | 18.3512 | 18.3512 | 7.2591 | 0.0070622 | 0.0070127 | 0.0082 | 0.0165 | 1.7591
1431 | - | - | 13 | 0.82017 | 70.84 | 77.785 | 23.7077 | 18.3677 | 18.3677 | 7.2661 | 0.0070127 | 0.0069638 | 0.0165 | 0.0071 | 1.6839
1441 | - | - | 13 | 0.82017 | 70.84 | 77.8083 | 23.7148 | 18.3748 | 18.3748 | 7.2731 | 0.0069638 | 0.0069157 | 0.0071 | 0.0211 | 2.0388
1451 | - | - | 13 | 0.82017 | 70.84 | 77.8775 | 23.7359 | 18.3959 | 18.3959 | 7.28 | 0.0069157 | 0.0068682 | 0.0211 | 0.0149 | 2.6087 | 0.053668 | 0.050934 | 0.107 | 0.0751 | 1.7273
1461 | - | - | 13 | 0.82017 | 70.84 | 77.9264 | 23.7508 | 18.4108 | 18.4108 | 7.2869 | 0.0068682 | 0.0068213 | 0.0149 | 0.0172 | 2.3461
1471 | - | - | 13 | 0.82017 | 70.84 | 77.9828 | 23.768 | 18.428 | 18.428 | 7.2937 | 0.0068213 | 0.0067751 | 0.0172 | 0.0214 | 2.8412
1481 | - | - | 13 | 0.82017 | 70.84 | 78.053 | 23.7894 | 18.4494 | 18.4494 | 7.3005 | 0.0067751 | 0.0067295 | 0.0214 | 0.0099 | 2.312
1491 | - | - | 13 | 0.82017 | 70.84 | 78.0855 | 23.7993 | 18.4593 | 18.4593 | 7.3072 | 0.0067295 | 0.0066845 | 0.0099 | 0.0187 | 2.1365
1501 | - | - | 13 | 0.82017 | 70.84 | 78.1469 | 23.818 | 18.478 | 18.478 | 7.3139 | 0.0066845 | 0.0066401 | 0.0187 | 0.0101 | 2.1572
1511 | - | - | 13 | 0.82017 | 70.84 | 78.18 | 23.8281 | 18.4881 | 18.4881 | 7.3205 | 0.0066401 | 0.0065963 | 0.0101 | 0.0017 | 0.8873
1521 | - | - | 13 | 0.82017 | 70.84 | 78.1856 | 23.8298 | 18.4898 | 18.4898 | 7.3271 | 0.0065963 | 0.0065531 | 0.0017 | 0.0131 | 1.1312
1531 | - | - | 13 | 0.82017 | 70.84 | 78.2286 | 23.8429 | 18.5029 | 18.5029 | 7.3337 | 0.0065531 | 0.0065104 | 0.0131 | 0.01 | 1.7668 | 0.050934 | 0.048465 | 0.0751 | 0.1105 | 1.8872
1541 | - | - | 13 | 0.82017 | 70.84 | 78.2614 | 23.8529 | 18.5129 | 18.5129 | 7.3402 | 0.0065104 | 0.0064683 | 0.01 | 0.0019 | 0.91285
1551 | - | - | 13 | 0.82017 | 70.84 | 78.2676 | 23.8548 | 18.5148 | 18.5148 | 7.3467 | 0.0064683 | 0.0064268 | 0.0019 | 0.0181 | 1.5591
1561 | - | - | 13 | 0.82017 | 70.84 | 78.327 | 23.8729 | 18.5329 | 18.5329 | 7.3531 | 0.0064268 | 0.0063857 | 0.0181 | 0.0183 | 2.8411
1571 | - | - | 13 | 0.82017 | 70.84 | 78.387 | 23.8912 | 18.5512 | 18.5512 | 7.3595 | 0.0063857 | 0.0063452 | 0.0183 | 0.005 | 1.8236
1581 | - | - | 13 | 0.82017 | 70.84 | 78.4034 | 23.8962 | 18.5562 | 18.5562 | 7.3658 | 0.0063452 | 0.0063052 | 0.005 | 0.0004 | 0.42457
1591 | - | - | 13 | 0.82017 | 70.84 | 78.4047 | 23.8966 | 18.5566 | 18.5566 | 7.3721 | 0.0063052 | 0.0062657 | 0.0004 | 0.0122 | 1.0082
1601 | - | - | 13 | 0.82017 | 70.84 | 78.4448 | 23.9088 | 18.5688 | 18.5688 | 7.3784 | 0.0062657 | 0.0062267 | 0.0122 | 0.0092 | 1.7116
1611 | - | - | 13 | 0.82017 | 70.84 | 78.475 | 23.918 | 18.578 | 18.578 | 7.3846 | 0.0062267 | 0.0061881 | 0.0092 | 0.0361 | 3.6624 | 0.048465 | 0.046224 | 0.1105 | 0.0583 | 1.7586
1621 | - | - | 13 | 0.82017 | 70.84 | 78.5934 | 23.9541 | 18.6141 | 18.6141 | 7.3908 | 0.0061881 | 0.0061501 | 0.0361 | 0.0249 | 4.9385
1631 | - | - | 13 | 0.82017 | 70.84 | 78.6751 | 23.979 | 18.639 | 18.639 | 7.3969 | 0.0061501 | 0.0061125 | 0.0249 | 0.0113 | 2.9453
1641 | - | - | 13 | 0.82017 | 70.84 | 78.7122 | 23.9903 | 18.6503 | 18.6503 | 7.4031 | 0.0061125 | 0.0060754 | 0.0113 | 0.0001 | 0.92978
1651 | - | - | 13 | 0.82017 | 70.84 | 78.7125 | 23.9904 | 18.6504 | 18.6504 | 7.4091 | 0.0060754 | 0.0060387 | 0.0001 | 0.0074 | 0.62278
1661 | - | - | 13 | 0.82017 | 70.84 | 78.7368 | 23.9978 | 18.6578 | 18.6578 | 7.4152 | 0.0060387 | 0.0060024 | 0.0074 | -0.0023 | 0.41871
1671 | - | - | 13 | 0.82017 | 70.84 | 78.7292 | 23.9955 | 18.6555 | 18.6555 | 7.4212 | 0.0060024 | 0.0059666 | -0.0023 | 0.0111 | 0.74194
1681 | - | - | 13 | 0.82017 | 70.84 | 78.7657 | 24.0066 | 18.6666 | 18.6666 | 7.4271 | 0.0059666 | 0.0059312 | 0.0111 | 0.0219 | 2.7791
1691 | - | - | 13 | 0.82017 | 70.84 | 78.8375 | 24.0285 | 18.6885 | 18.6885 | 7.4331 | 0.0059312 | 0.0058962 | 0.0219 | -0.0031 | 1.577 | 0.046224 | 0.044182 | 0.0583 | 0.0469 | 1.1591
1701 | - | - | 13 | 0.82017 | 70.84 | 78.8273 | 24.0254 | 18.6854 | 18.6854 | 7.439 | 0.0058962 | 0.0058617 | -0.0031 | 0.0098 | 0.57629
1711 | - | - | 13 | 0.82017 | 70.84 | 78.8595 | 24.0352 | 18.6952 | 18.6952 | 7.4448 | 0.0058617 | 0.0058275 | 0.0098 | 0.0021 | 1.0142
1721 | - | - | 13 | 0.82017 | 70.84 | 78.8664 | 24.0373 | 18.6973 | 18.6973 | 7.4507 | 0.0058275 | 0.0057938 | 0.0021 | 0.0105 | 1.0884
1731 | - | - | 13 | 0.82017 | 70.84 | 78.9008 | 24.0478 | 18.7078 | 18.7078 | 7.4565 | 0.0057938 | 0.0057604 | 0.0105 | 0.0061 | 1.4345
1741 | - | - | 13 | 0.82017 | 70.84 | 78.9208 | 24.0539 | 18.7139 | 18.7139 | 7.4622 | 0.0057604 | 0.0057274 | 0.0061 | 0.0062 | 1.0708
1751 | - | - | 13 | 0.82017 | 70.84 | 78.9412 | 24.0601 | 18.7201 | 18.7201 | 7.4679 | 0.0057274 | 0.0056948 | 0.0062 | 0.0184 | 2.1598
1761 | - | - | 13 | 0.82017 | 70.84 | 79.0016 | 24.0785 | 18.7385 | 18.7385 | 7.4736 | 0.0056948 | 0.0056625 | 0.0184 | 0.0083 | 2.3459
1771 | - | - | 13 | 0.82017 | 70.84 | 79.0288 | 24.0868 | 18.7468 | 18.7468 | 7.4793 | 0.0056625 | 0.0056306 | 0.0083 | 0.0081 | 1.4521 | 0.044182 | 0.042312 | 0.0469 | 0.0656 | 1.3112
1781 | - | - | 13 | 0.82017 | 70.84 | 79.0554 | 24.0949 | 18.7549 | 18.7549 | 7.4849 | 0.0056306 | 0.0055991 | 0.0081 | 0.0047 | 1.1381
1791 | - | - | 13 | 0.82017 | 70.84 | 79.0708 | 24.0996 | 18.7596 | 18.7596 | 7.4905 | 0.0055991 | 0.0055679 | 0.0047 | 0.0052 | 0.8868
1801 | - | - | 13 | 0.82017 | 70.84 | 79.0878 | 24.1048 | 18.7648 | 18.7648 | 7.4961 | 0.0055679 | 0.0055371 | 0.0052 | 0.0055 | 0.96369
1811 | - | - | 13 | 0.82017 | 70.84 | 79.1059 | 24.1103 | 18.7703 | 18.7703 | 7.5016 | 0.0055371 | 0.0055066 | 0.0055 | 0.006 | 1.0416
1821 | - | - | 13 | 0.82017 | 70.84 | 79.1256 | 24.1163 | 18.7763 | 18.7763 | 7.5071 | 0.0055066 | 0.0054765 | 0.006 | 0.0071 | 1.1933
1831 | - | - | 13 | 0.82017 | 70.84 | 79.1489 | 24.1234 | 18.7834 | 18.7834 | 7.5126 | 0.0054765 | 0.0054466 | 0.0071 | 0.0035 | 0.96863
1841 | - | - | 13 | 0.82017 | 70.84 | 79.1604 | 24.1269 | 18.7869 | 18.7869 | 7.5181 | 0.0054466 | 0.0054171 | 0.0035 | 0.0068 | 0.94977
1851 | - | - | 13 | 0.82017 | 70.84 | 79.1827 | 24.1337 | 18.7937 | 18.7937 | 7.5235 | 0.0054171 | 0.0053879 | 0.0068 | 0.0009 | 0.70969 | 0.042312 | 0.040594 | 0.0656 | 0.043 | 1.2997
1861 | - | - | 13 | 0.82017 | 70.84 | 79.1856 | 24.1346 | 18.7946 | 18.7946 | 7.5289 | 0.0053879 | 0.0053591 | 0.0009 | 0.0118 | 1.1872
1871 | - | - | 13 | 0.82017 | 70.84 | 79.2243 | 24.1464 | 18.8064 | 18.8064 | 7.5342 | 0.0053591 | 0.0053305 | 0.0118 | 0.0111 | 2.142
1881 | - | - | 13 | 0.82017 | 70.84 | 79.2608 | 24.1575 | 18.8175 | 18.8175 | 7.5396 | 0.0053305 | 0.0053022 | 0.0111 | -0.0028 | 0.77367
1891 | - | - | 13 | 0.82017 | 70.84 | 79.2516 | 24.1547 | 18.8147 | 18.8147 | 7.5449 | 0.0053022 | 0.0052743 | -0.0028 | 0.0038 | 0.09785
1901 | - | - | 13 | 0.82017 | 70.84 | 79.264 | 24.1585 | 18.8185 | 18.8185 | 7.5501 | 0.0052743 | 0.0052466 | 0.0038 | 0.0343 | 3.6367
1911 | - | - | 13 | 0.82017 | 70.84 | 79.3766 | 24.1928 | 18.8528 | 18.8528 | 7.5554 | 0.0052466 | 0.0052192 | 0.0343 | -0.0055 | 2.732
1921 | - | - | 13 | 0.82017 | 70.84 | 79.3585 | 24.1873 | 18.8473 | 18.8473 | 7.5606 | 0.0052192 | 0.0051921 | -0.0055 | 0.012 | 0.63308
1931 | - | - | 13 | 0.82017 | 70.84 | 79.3979 | 24.1993 | 18.8593 | 18.8593 | 7.5658 | 0.0051921 | 0.0051653 | 0.012 | 0.0042 | 1.5602 | 0.040594 | 0.03901 | 0.043 | 0.0648 | 1.3662
1941 | - | - | 13 | 0.82017 | 70.84 | 79.4117 | 24.2035 | 18.8635 | 18.8635 | 7.571 | 0.0051653 | 0.0051388 | 0.0042 | 0.0094 | 1.3225
1951 | - | - | 13 | 0.82017 | 70.84 | 79.4425 | 24.2129 | 18.8729 | 18.8729 | 7.5761 | 0.0051388 | 0.0051125 | 0.0094 | -0.0037 | 0.54949
1961 | - | - | 13 | 0.82017 | 70.84 | 79.4304 | 24.2092 | 18.8692 | 18.8692 | 7.5812 | 0.0051125 | 0.0050865 | -0.0037 | 0.0067 | 0.29935
1971 | - | - | 13 | 0.82017 | 70.84 | 79.4524 | 24.2159 | 18.8759 | 18.8759 | 7.5863 | 0.0050865 | 0.0050607 | 0.0067 | 0.0093 | 1.5781
1981 | - | - | 13 | 0.82017 | 70.84 | 79.4829 | 24.2252 | 18.8852 | 18.8852 | 7.5914 | 0.0050607 | 0.0050353 | 0.0093 | 0.0096 | 1.8722
1991 | - | - | 13 | 0.82017 | 70.84 | 79.5144 | 24.2348 | 18.8948 | 18.8948 | 7.5964 | 0.0050353 | 0.00501 | 0.0096 | 0.0045 | 1.4011
2001 | - | - | 13 | 0.82017 | 70.84 | 79.5291 | 24.2393 | 18.8993 | 18.8993 | 7.6014 | 0.00501 | 0.0049851 | 0.0045 | 0.003 | 0.74963
2011 | - | - | 13 | 0.82017 | 70.84 | 79.539 | 24.2423 | 18.9023 | 18.9023 | 7.6064 | 0.0049851 | 0.0049603 | 0.003 | 0.0028 | 0.58309 | 0.03901 | 0.037545 | 0.0648 | 0.0346 | 1.2842
2021 | - | - | 13 | 0.82017 | 70.84 | 79.5482 | 24.2451 | 18.9051 | 18.9051 | 7.6113 | 0.0049603 | 0.0049358 | 0.0028 | -0.0071 | -0.43947
2031 | - | - | 13 | 0.82017 | 70.84 | 79.5249 | 24.238 | 18.898 | 18.898 | 7.6163 | 0.0049358 | 0.0049116 | -0.0071 | 0.0139 | 0.70104
2041 | - | - | 13 | 0.82017 | 70.84 | 79.5705 | 24.2519 | 18.9119 | 18.9119 | 7.6212 | 0.0049116 | 0.0048876 | 0.0139 | -0.0026 | 1.1449
2051 | - | - | 13 | 0.82017 | 70.84 | 79.562 | 24.2493 | 18.9093 | 18.9093 | 7.6261 | 0.0048876 | 0.0048638 | -0.0026 | 0.0074 | 0.49724
2061 | - | - | 13 | 0.82017 | 70.84 | 79.5862 | 24.2567 | 18.9167 | 18.9167 | 7.6309 | 0.0048638 | 0.0048403 | 0.0074 | 0.0173 | 2.5503
2071 | - | - | 13 | 0.82017 | 70.84 | 79.643 | 24.274 | 18.934 | 18.934 | 7.6358 | 0.0048403 | 0.004817 | 0.0173 | 0.0093 | 2.7504
2081 | - | - | 13 | 0.82017 | 70.84 | 79.6735 | 24.2833 | 18.9433 | 18.9433 | 7.6406 | 0.004817 | 0.0047939 | 0.0093 | 0.0238 | 3.4513
2091 | - | - | 13 | 0.82017 | 70.84 | 79.7516 | 24.3071 | 18.9671 | 18.9671 | 7.6454 | 0.0047939 | 0.004771 | 0.0238 | -0.0006 | 2.4134 | 0.037545 | 0.036187 | 0.0346 | 0.0685 | 1.4162
2101 | - | - | 13 | 0.82017 | 70.84 | 79.7496 | 24.3065 | 18.9665 | 18.9665 | 7.6502 | 0.004771 | 0.0047483 | -0.0006 | 0.0088 | 0.86611
2111 | - | - | 13 | 0.82017 | 70.84 | 79.7785 | 24.3153 | 18.9753 | 18.9753 | 7.6549 | 0.0047483 | 0.0047259 | 0.0088 | 0.0192 | 2.9606
2121 | - | - | 13 | 0.82017 | 70.84 | 79.8415 | 24.3345 | 18.9945 | 18.9945 | 7.6596 | 0.0047259 | 0.0047037 | 0.0192 | -0.0019 | 1.8241
2131 | - | - | 13 | 0.82017 | 70.84 | 79.8353 | 24.3326 | 18.9926 | 18.9926 | 7.6643 | 0.0047037 | 0.0046817 | -0.0019 | 0.0124 | 1.1259
2141 | - | - | 13 | 0.82017 | 70.84 | 79.8759 | 24.345 | 19.005 | 19.005 | 7.669 | 0.0046817 | 0.0046598 | 0.0124 | -0.001 | 1.2137
2151 | - | - | 13 | 0.82017 | 70.84 | 79.8727 | 24.344 | 19.004 | 19.004 | 7.6737 | 0.0046598 | 0.0046382 | -0.001 | 0.0024 | 0.15227
2161 | - | - | 13 | 0.82017 | 70.84 | 79.8805 | 24.3464 | 19.0064 | 19.0064 | 7.6783 | 0.0046382 | 0.0046168 | 0.0024 | -0.0047 | -0.25207
2171 | - | - | 13 | 0.82017 | 70.84 | 79.8651 | 24.3417 | 19.0017 | 19.0017 | 7.6829 | 0.0046168 | 0.0045956 | -0.0047 | 0.0037 | -0.10435 | 0.036187 | 0.034923 | 0.0685 | 0.4007 | 6.7686
2181 | - | - | 13 | 0.82017 | 70.84 | 79.8773 | 24.3454 | 19.0054 | 19.0054 | 7.6875 | 0.0045956 | 0.0045746 | 0.0037 | -0.0007 | 0.32495
2191 | - | - | 13 | 0.82017 | 70.84 | 79.875 | 24.3447 | 19.0047 | 19.0047 | 7.6921 | 0.0045746 | 0.0045537 | -0.0007 | 0.0007 | 0.0007
2201 | - | - | 13 | 0.82017 | 70.84 | 79.8773 | 24.3454 | 19.0054 | 19.0054 | 7.6967 | 0.0045537 | 0.0045331 | 0.0007 | 0.0102 | 1.2043
2211 | - | - | 13 | 0.82017 | 70.84 | 79.9107 | 24.3556 | 19.0156 | 19.0156 | 7.7012 | 0.0045331 | 0.0045126 | 0.0102 | 0.0099 | 2.2219
2221 | - | - | 13 | 0.82017 | 70.84 | 79.9432 | 24.3655 | 19.0255 | 19.0255 | 7.7057 | 0.0045126 | 0.0044924 | 0.0099 | 0.0154 | 2.8123
2231 | - | - | 13 | 0.82017 | 70.84 | 79.9937 | 24.3809 | 19.0409 | 19.0409 | 7.7102 | 0.0044924 | 0.0044723 | 0.0154 | 0.0132 | 3.1892
2241 | - | - | 13 | 0.82017 | 70.84 | 80.037 | 24.3941 | 19.0541 | 19.0541 | 7.7147 | 0.0044723 | 0.0044524 | 0.0132 | 0.0161 | 3.2845
2251 | - | - | 13 | 0.82017 | 70.84 | 80.0899 | 24.4102 | 19.0702 | 19.0702 | 7.7191 | 0.0044524 | 0.0044326 | 0.0161 | 0.0097 | 2.9006 | 0.034923 | 0.033744 | 0.4007 | 0.1398 | 7.7455
2261 | - | - | 13 | 0.82017 | 70.84 | 80.1217 | 24.4199 | 19.0799 | 19.0799 | 7.7236 | 0.0044326 | 0.0044131 | 0.0097 | 0.0181 | 3.147
2271 | - | - | 13 | 0.82017 | 70.84 | 80.1811 | 24.438 | 19.098 | 19.098 | 7.728 | 0.0044131 | 0.0043937 | 0.0181 | 0.012 | 3.4148
2281 | - | - | 13 | 0.82017 | 70.84 | 80.2204 | 24.45 | 19.11 | 19.11 | 7.7324 | 0.0043937 | 0.0043745 | 0.012 | 0.0083 | 2.3134
2291 | - | - | 13 | 0.82017 | 70.84 | 80.2477 | 24.4583 | 19.1183 | 19.1183 | 7.7367 | 0.0043745 | 0.0043554 | 0.0083 | 0.1419 | 17.2723
2301 | - | - | 13 | 0.82017 | 70.84 | 80.7133 | 24.6002 | 19.2602 | 19.2602 | 7.7411 | 0.0043554 | 0.0043365 | 0.1419 | 0.1061 | 28.5146
2311 | - | - | 13 | 0.82017 | 70.84 | 81.0614 | 24.7063 | 19.3663 | 19.3663 | 7.7454 | 0.0043365 | 0.0043178 | 0.1061 | 0.0636 | 19.5876
2321 | - | - | 13 | 0.82017 | 70.84 | 81.27 | 24.7699 | 19.4299 | 19.4299 | 7.7498 | 0.0043178 | 0.0042992 | 0.0636 | 0.041 | 12.1276
2331 | - | - | 13 | 0.82017 | 70.84 | 81.4046 | 24.8109 | 19.4709 | 19.4709 | 7.7541 | 0.0042992 | 0.0042808 | 0.041 | 0.0333 | 8.6558 | 0.033744 | 0.032643 | 0.1398 | 0.1012 | 3.6129
2341 | - | - | 13 | 0.82017 | 70.84 | 81.5138 | 24.8442 | 19.5042 | 19.5042 | 7.7583 | 0.0042808 | 0.0042626 | 0.0333 | 0.0353 | 8.0307
2351 | - | - | 13 | 0.82017 | 70.84 | 81.6296 | 24.8795 | 19.5395 | 19.5395 | 7.7626 | 0.0042626 | 0.0042445 | 0.0353 | 0.0185 | 6.3158
2361 | - | - | 13 | 0.82017 | 70.84 | 81.6903 | 24.898 | 19.558 | 19.558 | 7.7668 | 0.0042445 | 0.0042265 | 0.0185 | 0.0209 | 4.6524
2371 | - | - | 13 | 0.82017 | 70.84 | 81.7589 | 24.9189 | 19.5789 | 19.5789 | 7.7711 | 0.0042265 | 0.0042088 | 0.0209 | 0.0185 | 4.6697
2381 | - | - | 13 | 0.82017 | 70.84 | 81.8196 | 24.9374 | 19.5974 | 19.5974 | 7.7753 | 0.0042088 | 0.0041911 | 0.0185 | 0.0084 | 3.1974
2391 | - | - | 13 | 0.82017 | 70.84 | 81.8472 | 24.9458 | 19.6058 | 19.6058 | 7.7795 | 0.0041911 | 0.0041736 | 0.0084 | -0.0026 | 0.68789
2401 | - | - | 13 | 0.82017 | 70.84 | 81.8386 | 24.9432 | 19.6032 | 19.6032 | 7.7836 | 0.0041736 | 0.0041563 | -0.0026 | 0.0075 | 0.5933
2411 | - | - | 13 | 0.82017 | 70.84 | 81.8632 | 24.9507 | 19.6107 | 19.6107 | 7.7878 | 0.0041563 | 0.0041391 | 0.0075 | 0.0028 | 1.2393 | 0.032643 | 0.031611 | 0.1012 | 0.072 | 2.6824
2421 | - | - | 13 | 0.82017 | 70.84 | 81.8724 | 24.9535 | 19.6135 | 19.6135 | 7.7919 | 0.0041391 | 0.004122 | 0.0028 | 0.0272 | 3.6437
2431 | - | - | 13 | 0.82017 | 70.84 | 81.9617 | 24.9807 | 19.6407 | 19.6407 | 7.7961 | 0.004122 | 0.0041051 | 0.0272 | 0.0137 | 4.9647
2441 | - | - | 13 | 0.82017 | 70.84 | 82.0066 | 24.9944 | 19.6544 | 19.6544 | 7.8002 | 0.0041051 | 0.0040883 | 0.0137 | 0.02 | 4.1162
2451 | - | - | 13 | 0.82017 | 70.84 | 82.0722 | 25.0144 | 19.6744 | 19.6744 | 7.8043 | 0.0040883 | 0.0040717 | 0.02 | 0.0092 | 3.5731
2461 | - | - | 13 | 0.82017 | 70.84 | 82.1024 | 25.0236 | 19.6836 | 19.6836 | 7.8083 | 0.0040717 | 0.0040552 | 0.0092 | 0.009 | 2.2394
2471 | - | - | 13 | 0.82017 | 70.84 | 82.132 | 25.0326 | 19.6926 | 19.6926 | 7.8124 | 0.0040552 | 0.0040388 | 0.009 | 0.0052 | 1.7525
2481 | - | - | 13 | 0.82017 | 70.84 | 82.149 | 25.0378 | 19.6978 | 19.6978 | 7.8164 | 0.0040388 | 0.0040225 | 0.0052 | 0.0141 | 2.3986
2491 | - | - | 13 | 0.82017 | 70.84 | 82.1953 | 25.0519 | 19.7119 | 19.7119 | 7.8204 | 0.0040225 | 0.0040064 | 0.0141 | 0.0047 | 2.3368 | 0.031611 | 0.030642 | 0.072 | 0.0248 | 1.5321
2501 | - | - | 13 | 0.82017 | 70.84 | 82.2107 | 25.0566 | 19.7166 | 19.7166 | 7.8244 | 0.0040064 | 0.0039904 | 0.0047 | 0.0124 | 2.1422
2511 | - | - | 13 | 0.82017 | 70.84 | 82.2514 | 25.069 | 19.729 | 19.729 | 7.8284 | 0.0039904 | 0.0039746 | 0.0124 | 0.0116 | 3.0128
2521 | - | - | 13 | 0.82017 | 70.84 | 82.2894 | 25.0806 | 19.7406 | 19.7406 | 7.8324 | 0.0039746 | 0.0039588 | 0.0116 | 0.0103 | 2.7599
2531 | - | - | 13 | 0.82017 | 70.84 | 82.3232 | 25.0909 | 19.7509 | 19.7509 | 7.8364 | 0.0039588 | 0.0039432 | 0.0103 | -0.0003 | 1.2602
2541 | - | - | 13 | 0.82017 | 70.84 | 82.3223 | 25.0906 | 19.7506 | 19.7506 | 7.8403 | 0.0039432 | 0.0039277 | -0.0003 | 0.012 | 1.4926
2551 | - | - | 13 | 0.82017 | 70.84 | 82.3616 | 25.1026 | 19.7626 | 19.7626 | 7.8442 | 0.0039277 | 0.0039124 | 0.012 | 0.0096 | 2.7539
2561 | - | - | 13 | 0.82017 | 70.84 | 82.3931 | 25.1122 | 19.7722 | 19.7722 | 7.8482 | 0.0039124 | 0.0038971 | 0.0096 | 0.0117 | 2.7285
2571 | - | - | 13 | 0.82017 | 70.84 | 82.4315 | 25.1239 | 19.7839 | 19.7839 | 7.8521 | 0.0038971 | 0.003882 | 0.0117 | 0.0043 | 2.0531 | 0.030642 | 0.029731 | 0.0248 | 0.0461 | 1.1856
2581 | - | - | 13 | 0.82017 | 70.84 | 82.4456 | 25.1282 | 19.7882 | 19.7882 | 7.8559 | 0.003882 | 0.003867 | 0.0043 | 0.0049 | 1.1876
2591 | - | - | 13 | 0.82017 | 70.84 | 82.4617 | 25.1331 | 19.7931 | 19.7931 | 7.8598 | 0.003867 | 0.0038521 | 0.0049 | 0.0045 | 1.2176
2601 | - | - | 13 | 0.82017 | 70.84 | 82.4765 | 25.1376 | 19.7976 | 19.7976 | 7.8637 | 0.0038521 | 0.0038373 | 0.0045 | 0.0053 | 1.2749
2611 | - | - | 13 | 0.82017 | 70.84 | 82.4939 | 25.1429 | 19.8029 | 19.8029 | 7.8675 | 0.0038373 | 0.0038226 | 0.0053 | -0.0031 | 0.28301
2621 | - | - | 13 | 0.82017 | 70.84 | 82.4837 | 25.1398 | 19.7998 | 19.7998 | 7.8713 | 0.0038226 | 0.0038081 | -0.0031 | 0.004 | 0.1215
2631 | - | - | 13 | 0.82017 | 70.84 | 82.4968 | 25.1438 | 19.8038 | 19.8038 | 7.8751 | 0.0038081 | 0.0037936 | 0.004 | 0.015 | 2.505
2641 | - | - | 13 | 0.82017 | 70.84 | 82.546 | 25.1588 | 19.8188 | 19.8188 | 7.8789 | 0.0037936 | 0.0037793 | 0.015 | -0.0101 | 0.6345
2651 | - | - | 13 | 0.82017 | 70.84 | 82.5129 | 25.1487 | 19.8087 | 19.8087 | 7.8827 | 0.0037793 | 0.0037651 | -0.0101 | 0.0075 | -0.33583 | 0.029731 | 0.028872 | 0.0461 | 0.0462 | 1.5757
2661 | - | - | 13 | 0.82017 | 70.84 | 82.5375 | 25.1562 | 19.8162 | 19.8162 | 7.8865 | 0.0037651 | 0.0037509 | 0.0075 | 0.0041 | 1.5417
2671 | - | - | 13 | 0.82017 | 70.84 | 82.5509 | 25.1603 | 19.8203 | 19.8203 | 7.8902 | 0.0037509 | 0.0037369 | 0.0041 | 0.0095 | 1.819
2681 | - | - | 13 | 0.82017 | 70.84 | 82.5821 | 25.1698 | 19.8298 | 19.8298 | 7.8939 | 0.0037369 | 0.003723 | 0.0095 | 0.0058 | 2.0491
2691 | - | - | 13 | 0.82017 | 70.84 | 82.6011 | 25.1756 | 19.8356 | 19.8356 | 7.8977 | 0.003723 | 0.0037092 | 0.0058 | 0.0009 | 0.89904
2701 | - | - | 13 | 0.82017 | 70.84 | 82.6041 | 25.1765 | 19.8365 | 19.8365 | 7.9014 | 0.0037092 | 0.0036955 | 0.0009 | 0.0125 | 1.8155
2711 | - | - | 13 | 0.82017 | 70.84 | 82.6451 | 25.189 | 19.849 | 19.849 | 7.9051 | 0.0036955 | 0.0036819 | 0.0125 | -0.0003 | 1.6473
2721 | - | - | 13 | 0.82017 | 70.84 | 82.6441 | 25.1887 | 19.8487 | 19.8487 | 7.9088 | 0.0036819 | 0.0036684 | -0.0003 | 0.0061 | 0.79229
2731 | - | - | 13 | 0.82017 | 70.84 | 82.6641 | 25.1948 | 19.8548 | 19.8548 | 7.9124 | 0.0036684 | 0.003655 | 0.0061 | 0 | 0.82991 | 0.028872 | 0.028062 | 0.0462 | 0.0217 | 1.1808
2741 | - | - | 13 | 0.82017 | 70.84 | 82.6641 | 25.1948 | 19.8548 | 19.8548 | 7.9161 | 0.003655 | 0.0036417 | 0 | 0.0179 | 2.4622
2751 | - | - | 13 | 0.82017 | 70.84 | 82.7229 | 25.2127 | 19.8727 | 19.8727 | 7.9197 | 0.0036417 | 0.0036285 | 0.0179 | 0.0017 | 2.6879
2761 | - | - | 13 | 0.82017 | 70.84 | 82.7284 | 25.2144 | 19.8744 | 19.8744 | 7.9233 | 0.0036285 | 0.0036153 | 0.0017 | 0.0023 | 0.5525
2771 | - | - | 13 | 0.82017 | 70.84 | 82.736 | 25.2167 | 19.8767 | 19.8767 | 7.927 | 0.0036153 | 0.0036023 | 0.0023 | 0.0092 | 1.5968
2781 | - | - | 13 | 0.82017 | 70.84 | 82.7662 | 25.2259 | 19.8859 | 19.8859 | 7.9306 | 0.0036023 | 0.0035894 | 0.0092 | 0.0058 | 2.0841
2791 | - | - | 13 | 0.82017 | 70.84 | 82.7852 | 25.2317 | 19.8917 | 19.8917 | 7.9342 | 0.0035894 | 0.0035765 | 0.0058 | 0.0025 | 1.1566
2801 | - | - | 13 | 0.82017 | 70.84 | 82.7934 | 25.2342 | 19.8942 | 19.8942 | 7.9377 | 0.0035765 | 0.0035638 | 0.0025 | 0.0068 | 1.3046
2811 | - | - | 13 | 0.82017 | 70.84 | 82.8157 | 25.241 | 19.901 | 19.901 | 7.9413 | 0.0035638 | 0.0035511 | 0.0068 | 0.002 | 1.2344 | 0.028062 | 0.027296 | 0.0217 | -0.2626 | -4.4955
2821 | - | - | 13 | 0.82017 | 70.84 | 82.8223 | 25.243 | 19.903 | 19.903 | 7.9448 | 0.0035511 | 0.0035386 | 0.002 | 0.0026 | 0.64913
2831 | - | - | 13 | 0.82017 | 70.84 | 82.8308 | 25.2456 | 19.9056 | 19.9056 | 7.9484 | 0.0035386 | 0.0035261 | 0.0026 | 0.0078 | 1.4747
2841 | - | - | 13 | 0.82017 | 70.84 | 82.8564 | 25.2534 | 19.9134 | 19.9134 | 7.9519 | 0.0035261 | 0.0035137 | 0.0078 | 0.0049 | 1.8026
2851 | - | - | 13 | 0.82017 | 70.84 | 82.8725 | 25.2583 | 19.9183 | 19.9183 | 7.9554 | 0.0035137 | 0.0035014 | 0.0049 | 0.0007 | 0.79618
2861 | - | - | 13 | 0.82017 | 70.84 | 82.8748 | 25.259 | 19.919 | 19.919 | 7.9589 | 0.0035014 | 0.0034892 | 0.0007 | 0.0041 | 0.68834
2871 | - | - | 13 | 0.82017 | 70.84 | 82.8882 | 25.2631 | 19.9231 | 19.9231 | 7.9624 | 0.0034892 | 0.0034771 | 0.0041 | -0.0004 | 0.52889
2881 | - | - | 13 | 0.82017 | 70.84 | 82.8869 | 25.2627 | 19.9227 | 19.9227 | 7.9659 | 0.0034771 | 0.003465 | -0.0004 | 0 | -0.05742
2891 | - | - | 13 | 0.82017 | 70.84 | 82.8869 | 25.2627 | 19.9227 | 19.9227 | 7.9694 | 0.003465 | 0.003453 | 0 | 0.0059 | 0.8558 | 0.027296 | 0.026571 | -0.2626 | 0.044 | -3.9063
2901 | - | - | 13 | 0.82017 | 70.84 | 82.9063 | 25.2686 | 19.9286 | 19.9286 | 7.9728 | 0.003453 | 0.0034412 | 0.0059 | 0 | 0.85285
2911 | - | - | 13 | 0.82017 | 70.84 | 82.9063 | 25.2686 | 19.9286 | 19.9286 | 7.9763 | 0.0034412 | 0.0034294 | 0 | 0.0159 | 2.3222
2921 | - | - | 13 | 0.82017 | 70.84 | 82.9584 | 25.2845 | 19.9445 | 19.9445 | 7.9797 | 0.0034294 | 0.0034176 | 0.0159 | 0.0206 | 5.3332
2931 | - | - | 13 | 0.82017 | 70.84 | 83.026 | 25.3051 | 19.9651 | 19.9651 | 7.9831 | 0.0034176 | 0.003406 | 0.0206 | 0.0078 | 4.1556
2941 | - | - | 13 | 0.82017 | 70.84 | 83.0516 | 25.3129 | 19.9729 | 19.9729 | 7.9865 | 0.003406 | 0.0033944 | 0.0078 | -0.4015 | -58.0983
2951 | - | - | 13 | 0.82017 | 70.84 | 81.7343 | 24.9114 | 19.5714 | 19.5714 | 7.9899 | 0.0033944 | 0.003383 | -0.4015 | 0.0542 | -51.0164
2961 | - | - | 13 | 0.82017 | 70.84 | 81.9121 | 24.9656 | 19.6256 | 19.6256 | 7.9933 | 0.003383 | 0.0033715 | 0.0542 | 0.0345 | 13.1222
2971 | - | - | 13 | 0.82017 | 70.84 | 82.0253 | 25.0001 | 19.6601 | 19.6601 | 7.9967 | 0.0033715 | 0.0033602 | 0.0345 | 0.0227 | 8.4912 | 0.026571 | 0.025883 | 0.044 | 0.022 | 1.2477
2981 | - | - | 13 | 0.82017 | 70.84 | 82.0998 | 25.0228 | 19.6828 | 19.6828 | 8 | 0.0033602 | 0.003349 | 0.0227 | 0.009 | 4.718
2991 | - | - | 13 | 0.82017 | 70.84 | 82.1293 | 25.0318 | 19.6918 | 19.6918 | 8.0034 | 0.003349 | 0.0033378 | 0.009 | 0.0036 | 1.8816
3001 | - | - | 13 | 0.82017 | 70.84 | 82.1411 | 25.0354 | 19.6954 | 19.6954 | 8.0067 | 0.0033378 | 0.0033267 | 0.0036 | -0.0089 | -0.80152
3011 | - | - | 13 | 0.82017 | 70.84 | 82.1119 | 25.0265 | 19.6865 | 19.6865 | 8.01 | 0.0033267 | 0.0033157 | -0.0089 | 0.0142 | 0.80947
3021 | - | - | 13 | 0.82017 | 70.84 | 82.1585 | 25.0407 | 19.7007 | 19.7007 | 8.0133 | 0.0033157 | 0.0033047 | 0.0142 | -0.005 | 1.3801
3031 | - | - | 13 | 0.82017 | 70.84 | 82.1421 | 25.0357 | 19.6957 | 19.6957 | 8.0166 | 0.0033047 | 0.0032938 | -0.005 | -0.0019 | -1.0441
3041 | - | - | 13 | 0.82017 | 70.84 | 82.1359 | 25.0338 | 19.6938 | 19.6938 | 8.0199 | 0.0032938 | 0.003283 | -0.0019 | 0.0103 | 1.2833
3051 | - | - | 13 | 0.82017 | 70.84 | 82.1697 | 25.0441 | 19.7041 | 19.7041 | 8.0232 | 0.003283 | 0.0032723 | 0.0103 | -0.0027 | 1.1529 | 0.025883 | 0.02523 | 0.022 | 0.0111 | 0.64235
3061 | - | - | 13 | 0.82017 | 70.84 | 82.1608 | 25.0414 | 19.7014 | 19.7014 | 8.0265 | 0.0032723 | 0.0032616 | -0.0027 | -0.0039 | -1.0107
3071 | - | - | 13 | 0.82017 | 70.84 | 82.148 | 25.0375 | 19.6975 | 19.6975 | 8.0298 | 0.0032616 | 0.003251 | -0.0039 | 0.0058 | 0.2966
3081 | - | - | 13 | 0.82017 | 70.84 | 82.1671 | 25.0433 | 19.7033 | 19.7033 | 8.033 | 0.003251 | 0.0032404 | 0.0058 | -0.008 | -0.34581
3091 | - | - | 13 | 0.82017 | 70.84 | 82.1408 | 25.0353 | 19.6953 | 19.6953 | 8.0362 | 0.0032404 | 0.00323 | -0.008 | -0.002 | -1.5425
3101 | - | - | 13 | 0.82017 | 70.84 | 82.1343 | 25.0333 | 19.6933 | 19.6933 | 8.0395 | 0.00323 | 0.0032196 | -0.002 | 0.0017 | -0.044665
3111 | - | - | 13 | 0.82017 | 70.84 | 82.1398 | 25.035 | 19.695 | 19.695 | 8.0427 | 0.0032196 | 0.0032092 | 0.0017 | 0.0255 | 4.2429
3121 | - | - | 13 | 0.82017 | 70.84 | 82.2235 | 25.0605 | 19.7205 | 19.7205 | 8.0459 | 0.0032092 | 0.003199 | 0.0255 | 0.0056 | 4.8432
3131 | - | - | 13 | 0.82017 | 70.84 | 82.2419 | 25.0661 | 19.7261 | 19.7261 | 8.0491 | 0.003199 | 0.0031888 | 0.0056 | 0.006 | 1.8162 | 0.02523 | 0.024609 | 0.0111 | -0.0058 | 0.097925
3141 | - | - | 13 | 0.82017 | 70.84 | 82.2616 | 25.0721 | 19.7321 | 19.7321 | 8.0523 | 0.0031888 | 0.0031786 | 0.006 | -0.0039 | 0.32486
3151 | - | - | 13 | 0.82017 | 70.84 | 82.2488 | 25.0682 | 19.7282 | 19.7282 | 8.0555 | 0.0031786 | 0.0031686 | -0.0039 | 0.0068 | 0.46225
3161 | - | - | 13 | 0.82017 | 70.84 | 82.2711 | 25.075 | 19.735 | 19.735 | 8.0586 | 0.0031686 | 0.0031586 | 0.0068 | -0.0028 | 0.6274
3171 | - | - | 13 | 0.82017 | 70.84 | 82.2619 | 25.0722 | 19.7322 | 19.7322 | 8.0618 | 0.0031586 | 0.0031486 | -0.0028 | 0.0011 | -0.26759
3181 | - | - | 13 | 0.82017 | 70.84 | 82.2655 | 25.0733 | 19.7333 | 19.7333 | 8.065 | 0.0031486 | 0.0031387 | 0.0011 | -0.0038 | -0.43189
3191 | - | - | 13 | 0.82017 | 70.84 | 82.253 | 25.0695 | 19.7295 | 19.7295 | 8.0681 | 0.0031387 | 0.0031289 | -0.0038 | 0.0069 | 0.49996
3201 | - | - | 13 | 0.82017 | 70.84 | 82.2757 | 25.0764 | 19.7364 | 19.7364 | 8.0712 | 0.0031289 | 0.0031192 | 0.0069 | 0.0008 | 1.2293
3211 | - | - | 13 | 0.82017 | 70.84 | 82.2783 | 25.0772 | 19.7372 | 19.7372 | 8.0743 | 0.0031192 | 0.0031095 | 0.0008 | -0.0002 | 0.09583 | 0.024609 | 0.024018 | -0.0058 | 0.0094 | 0.081655
3221 | - | - | 13 | 0.82017 | 70.84 | 82.2776 | 25.077 | 19.737 | 19.737 | 8.0774 | 0.0031095 | 0.0030998 | -0.0002 | 0.0032 | 0.48485
3231 | - | - | 13 | 0.82017 | 70.84 | 82.2881 | 25.0802 | 19.7402 | 19.7402 | 8.0805 | 0.0030998 | 0.0030902 | 0.0032 | 0.0073 | 1.6983
3241 | - | - | 13 | 0.82017 | 70.84 | 82.3121 | 25.0875 | 19.7475 | 19.7475 | 8.0836 | 0.0030902 | 0.0030807 | 0.0073 | -0.0059 | 0.22027
3251 | - | - | 13 | 0.82017 | 70.84 | 82.2927 | 25.0816 | 19.7416 | 19.7416 | 8.0867 | 0.0030807 | 0.0030713 | -0.0059 | 0.0083 | 0.39722
3261 | - | - | 13 | 0.82017 | 70.84 | 82.32 | 25.0899 | 19.7499 | 19.7499 | 8.0898 | 0.0030713 | 0.0030619 | 0.0083 | -0.0039 | 0.71132
3271 | - | - | 13 | 0.82017 | 70.84 | 82.3072 | 25.086 | 19.746 | 19.746 | 8.0929 | 0.0030619 | 0.0030525 | -0.0039 | -0.0117 | -2.5553
3281 | - | - | 13 | 0.82017 | 70.84 | 82.2688 | 25.0743 | 19.7343 | 19.7343 | 8.0959 | 0.0030525 | 0.0030432 | -0.0117 | -0.0029 | -2.3907
3291 | - | - | 13 | 0.82017 | 70.84 | 82.2593 | 25.0714 | 19.7314 | 19.7314 | 8.0989 | 0.0030432 | 0.003034 | -0.0029 | 0.0089 | 0.9932 | 0.024018 | 0.023455 | 0.0094 | 0.0087 | 0.38103
3301 | - | - | 13 | 0.82017 | 70.84 | 82.2885 | 25.0803 | 19.7403 | 19.7403 | 8.102 | 0.003034 | 0.0030248 | 0.0089 | -0.0007 | 1.3486
3311 | - | - | 13 | 0.82017 | 70.84 | 82.2862 | 25.0796 | 19.7396 | 19.7396 | 8.105 | 0.0030248 | 0.0030157 | -0.0007 | 0.0049 | 0.69811
3321 | - | - | 13 | 0.82017 | 70.84 | 82.3022 | 25.0845 | 19.7445 | 19.7445 | 8.108 | 0.0030157 | 0.0030066 | 0.0049 | 0.0001 | 0.82785
3331 | - | - | 13 | 0.82017 | 70.84 | 82.3026 | 25.0846 | 19.7446 | 19.7446 | 8.111 | 0.0030066 | 0.0029976 | 0.0001 | -0.0012 | -0.18386
3341 | - | - | 13 | 0.82017 | 70.84 | 82.2986 | 25.0834 | 19.7434 | 19.7434 | 8.114 | 0.0029976 | 0.0029886 | -0.0012 | -0.0035 | -0.78629
3351 | - | - | 13 | 0.82017 | 70.84 | 82.2872 | 25.0799 | 19.7399 | 19.7399 | 8.117 | 0.0029886 | 0.0029797 | -0.0035 | 0.003 | -0.080525
3361 | - | - | 13 | 0.82017 | 70.84 | 82.297 | 25.0829 | 19.7429 | 19.7429 | 8.12 | 0.0029797 | 0.0029709 | 0.003 | -0.0021 | 0.1487
3371 | - | - | 13 | 0.82017 | 70.84 | 82.2901 | 25.0808 | 19.7408 | 19.7408 | 8.123 | 0.0029709 | 0.0029621 | -0.0021 | -0.0084 | -1.7729 | 0.023455 | 0.022917 | 0.0087 | 0.0152 | 0.51879
3381 | - | - | 13 | 0.82017 | 70.84 | 82.2625 | 25.0724 | 19.7324 | 19.7324 | 8.1259 | 0.0029621 | 0.0029533 | -0.0084 | 0.0056 | -0.46634
3391 | - | - | 13 | 0.82017 | 70.84 | 82.2809 | 25.078 | 19.738 | 19.738 | 8.1289 | 0.0029533 | 0.0029446 | 0.0056 | -0.0047 | 0.14745
3401 | - | - | 13 | 0.82017 | 70.84 | 82.2655 | 25.0733 | 19.7333 | 19.7333 | 8.1318 | 0.0029446 | 0.002936 | -0.0047 | 0.007 | 0.39697
3411 | - | - | 13 | 0.82017 | 70.84 | 82.2885 | 25.0803 | 19.7403 | 19.7403 | 8.1348 | 0.002936 | 0.0029274 | 0.007 | 0.0022 | 1.5667
3421 | - | - | 13 | 0.82017 | 70.84 | 82.2957 | 25.0825 | 19.7425 | 19.7425 | 8.1377 | 0.0029274 | 0.0029189 | 0.0022 | 0.0002 | 0.40952
3431 | - | - | 13 | 0.82017 | 70.84 | 82.2963 | 25.0827 | 19.7427 | 19.7427 | 8.1406 | 0.0029189 | 0.0029104 | 0.0002 | -0.0028 | -0.44753
3441 | - | - | 13 | 0.82017 | 70.84 | 82.2872 | 25.0799 | 19.7399 | 19.7399 | 8.1435 | 0.0029104 | 0.0029019 | -0.0028 | 0.0096 | 1.1761
3451 | - | - | 13 | 0.82017 | 70.84 | 82.3186 | 25.0895 | 19.7495 | 19.7495 | 8.1464 | 0.0029019 | 0.0028935 | 0.0096 | 0.0057 | 2.6381 | 0.022917 | 0.022404 | 0.0152 | 0.0373 | 1.1698
3461 | - | - | 13 | 0.82017 | 70.84 | 82.3374 | 25.0952 | 19.7552 | 19.7552 | 8.1493 | 0.0028935 | 0.0028852 | 0.0057 | 0.0022 | 1.3653
3471 | - | - | 13 | 0.82017 | 70.84 | 82.3446 | 25.0974 | 19.7574 | 19.7574 | 8.1522 | 0.0028852 | 0.0028769 | 0.0022 | -0.0054 | -0.55916
3481 | - | - | 13 | 0.82017 | 70.84 | 82.3269 | 25.092 | 19.752 | 19.752 | 8.1551 | 0.0028769 | 0.0028686 | -0.0054 | 0.0145 | 1.5938
3491 | - | - | 13 | 0.82017 | 70.84 | 82.3744 | 25.1065 | 19.7665 | 19.7665 | 8.1579 | 0.0028686 | 0.0028604 | 0.0145 | -0.0079 | 1.1408
3501 | - | - | 13 | 0.82017 | 70.84 | 82.3485 | 25.0986 | 19.7586 | 19.7586 | 8.1608 | 0.0028604 | 0.0028523 | -0.0079 | 0.0037 | -0.72941
3511 | - | - | 13 | 0.82017 | 70.84 | 82.3606 | 25.1023 | 19.7623 | 19.7623 | 8.1637 | 0.0028523 | 0.0028441 | 0.0037 | 0.006 | 1.704
3521 | - | - | 13 | 0.82017 | 70.84 | 82.3803 | 25.1083 | 19.7683 | 19.7683 | 8.1665 | 0.0028441 | 0.0028361 | 0.006 | -0.0036 | 0.41772
3531 | - | - | 13 | 0.82017 | 70.84 | 82.3685 | 25.1047 | 19.7647 | 19.7647 | 8.1693 | 0.0028361 | 0.0028281 | -0.0036 | 0.0098 | 1.1013 | 0.022404 | 0.021913 | 0.0373 | 0.0527 | 2.0391
3541 | - | - | 13 | 0.82017 | 70.84 | 82.4007 | 25.1145 | 19.7745 | 19.7745 | 8.1722 | 0.0028281 | 0.0028201 | 0.0098 | 0.0048 | 2.5824
3551 | - | - | 13 | 0.82017 | 70.84 | 82.4164 | 25.1193 | 19.7793 | 19.7793 | 8.175 | 0.0028201 | 0.0028122 | 0.0048 | 0.008 | 2.2742
3561 | - | - | 13 | 0.82017 | 70.84 | 82.4427 | 25.1273 | 19.7873 | 19.7873 | 8.1778 | 0.0028122 | 0.0028043 | 0.008 | -0.0016 | 1.1347
3571 | - | - | 13 | 0.82017 | 70.84 | 82.4374 | 25.1257 | 19.7857 | 19.7857 | 8.1806 | 0.0028043 | 0.0027964 | -0.0016 | 0.0032 | 0.28808
3581 | - | - | 13 | 0.82017 | 70.84 | 82.4479 | 25.1289 | 19.7889 | 19.7889 | 8.1834 | 0.0027964 | 0.0027886 | 0.0032 | 0.0038 | 1.2537
3591 | - | - | 13 | 0.82017 | 70.84 | 82.4604 | 25.1327 | 19.7927 | 19.7927 | 8.1862 | 0.0027886 | 0.0027809 | 0.0038 | -0.0002 | 0.64438
3601 | - | - | 13 | 0.82017 | 70.84 | 82.4597 | 25.1325 | 19.7925 | 19.7925 | 8.189 | 0.0027809 | 0.0027732 | -0.0002 | 0.0095 | 1.6793
3611 | - | - | 13 | 0.82017 | 70.84 | 82.4909 | 25.142 | 19.802 | 19.802 | 8.1917 | 0.0027732 | 0.0027655 | 0.0095 | 0 | 1.7105 | 0.021913 | 0.021443 | 0.0527 | 0.0351 | 2.0168
3621 | - | - | 13 | 0.82017 | 70.84 | 82.4909 | 25.142 | 19.802 | 19.802 | 8.1945 | 0.0027655 | 0.0027579 | 0 | 0.0119 | 2.1604
3631 | - | - | 13 | 0.82017 | 70.84 | 82.5299 | 25.1539 | 19.8139 | 19.8139 | 8.1973 | 0.0027579 | 0.0027503 | 0.0119 | 0.0116 | 4.2663
3641 | - | - | 13 | 0.82017 | 70.84 | 82.568 | 25.1655 | 19.8255 | 19.8255 | 8.2 | 0.0027503 | 0.0027427 | 0.0116 | 0.0126 | 4.4061
3651 | - | - | 13 | 0.82017 | 70.84 | 82.6093 | 25.1781 | 19.8381 | 19.8381 | 8.2028 | 0.0027427 | 0.0027352 | 0.0126 | -0.0015 | 2.0193
3661 | - | - | 13 | 0.82017 | 70.84 | 82.6044 | 25.1766 | 19.8366 | 19.8366 | 8.2055 | 0.0027352 | 0.0027278 | -0.0015 | 0.0117 | 1.8737
3671 | - | - | 13 | 0.82017 | 70.84 | 82.6428 | 25.1883 | 19.8483 | 19.8483 | 8.2082 | 0.0027278 | 0.0027203 | 0.0117 | 0.0049 | 3.0435
3681 | - | - | 13 | 0.82017 | 70.84 | 82.6589 | 25.1932 | 19.8532 | 19.8532 | 8.2109 | 0.0027203 | 0.002713 | 0.0049 | 0.0015 | 1.1762
3691 | - | - | 13 | 0.82017 | 70.84 | 82.6638 | 25.1947 | 19.8547 | 19.8547 | 8.2137 | 0.002713 | 0.0027056 | 0.0015 | 0.0131 | 2.7002 | 0.021443 | 0.020993 | 0.0351 | 0.0581 | 2.2083
3701 | - | - | 13 | 0.82017 | 70.84 | 82.7068 | 25.2078 | 19.8678 | 19.8678 | 8.2164 | 0.0027056 | 0.0026983 | 0.0131 | 0.0001 | 2.4362
3711 | - | - | 13 | 0.82017 | 70.84 | 82.7071 | 25.2079 | 19.8679 | 19.8679 | 8.2191 | 0.0026983 | 0.0026911 | 0.0001 | 0.0088 | 1.6557
3721 | - | - | 13 | 0.82017 | 70.84 | 82.736 | 25.2167 | 19.8767 | 19.8767 | 8.2217 | 0.0026911 | 0.0026838 | 0.0088 | -0.0074 | 0.25237
3731 | - | - | 13 | 0.82017 | 70.84 | 82.7117 | 25.2093 | 19.8693 | 19.8693 | 8.2244 | 0.0026838 | 0.0026767 | -0.0074 | -0.0003 | -1.4329
3741 | - | - | 13 | 0.82017 | 70.84 | 82.7107 | 25.209 | 19.869 | 19.869 | 8.2271 | 0.0026767 | 0.0026695 | -0.0003 | 0.0009 | 0.11283
3751 | - | - | 13 | 0.82017 | 70.84 | 82.7137 | 25.2099 | 19.8699 | 19.8699 | 8.2298 | 0.0026695 | 0.0026624 | 0.0009 | 0.0093 | 1.9172
3761 | - | - | 13 | 0.82017 | 70.84 | 82.7442 | 25.2192 | 19.8792 | 19.8792 | 8.2324 | 0.0026624 | 0.0026553 | 0.0093 | 0.0106 | 3.7428
3771 | - | - | 13 | 0.82017 | 70.84 | 82.779 | 25.2298 | 19.8898 | 19.8898 | 8.2351 | 0.0026553 | 0.0026483 | 0.0106 | 0.0106 | 3.9973 | 0.020993 | 0.020561 | 0.0581 | 0.0364 | 2.2638
3781 | - | - | 13 | 0.82017 | 70.84 | 82.8138 | 25.2404 | 19.9004 | 19.9004 | 8.2377 | 0.0026483 | 0.0026413 | 0.0106 | 0.0085 | 3.6098
3791 | - | - | 13 | 0.82017 | 70.84 | 82.8416 | 25.2489 | 19.9089 | 19.9089 | 8.2404 | 0.0026413 | 0.0026344 | 0.0085 | 0.0124 | 3.9635
3801 | - | - | 13 | 0.82017 | 70.84 | 82.8823 | 25.2613 | 19.9213 | 19.9213 | 8.243 | 0.0026344 | 0.0026274 | 0.0124 | 0.0078 | 3.8367
3811 | - | - | 13 | 0.82017 | 70.84 | 82.9079 | 25.2691 | 19.9291 | 19.9291 | 8.2456 | 0.0026274 | 0.0026205 | 0.0078 | 0.0093 | 3.2592
3821 | - | - | 13 | 0.82017 | 70.84 | 82.9384 | 25.2784 | 19.9384 | 19.9384 | 8.2483 | 0.0026205 | 0.0026137 | 0.0093 | 0.0118 | 4.0324
3831 | - | - | 13 | 0.82017 | 70.84 | 82.9771 | 25.2902 | 19.9502 | 19.9502 | 8.2509 | 0.0026137 | 0.0026069 | 0.0118 | 0.0027 | 2.7729
3841 | - | - | 13 | 0.82017 | 70.84 | 82.986 | 25.2929 | 19.9529 | 19.9529 | 8.2535 | 0.0026069 | 0.0026001 | 0.0027 | -0.005 | -0.44557
3851 | - | - | 13 | 0.82017 | 70.84 | 82.9696 | 25.2879 | 19.9479 | 19.9479 | 8.2561 | 0.0026001 | 0.0025934 | -0.005 | 0.0068 | 0.35249 | 0.020561 | 0.020147 | 0.0364 | -0.0017 | 0.83354
3861 | - | - | 13 | 0.82017 | 70.84 | 82.9919 | 25.2947 | 19.9547 | 19.9547 | 8.2587 | 0.0025934 | 0.0025867 | 0.0068 | 0.0068 | 2.6255
3871 | - | - | 13 | 0.82017 | 70.84 | 83.0142 | 25.3015 | 19.9615 | 19.9615 | 8.2613 | 0.0025867 | 0.00258 | 0.0068 | -0.002 | 0.92464
3881 | - | - | 13 | 0.82017 | 70.84 | 83.0077 | 25.2995 | 19.9595 | 19.9595 | 8.2638 | 0.00258 | 0.0025733 | -0.002 | -0.0018 | -0.73729
3891 | - | - | 13 | 0.82017 | 70.84 | 83.0018 | 25.2977 | 19.9577 | 19.9577 | 8.2664 | 0.0025733 | 0.0025667 | -0.0018 | 0.0102 | 1.6402
3901 | - | - | 13 | 0.82017 | 70.84 | 83.0352 | 25.3079 | 19.9679 | 19.9679 | 8.269 | 0.0025667 | 0.0025602 | 0.0102 | 0.0061 | 3.1773
3911 | - | - | 13 | 0.82017 | 70.84 | 83.0552 | 25.314 | 19.974 | 19.974 | 8.2715 | 0.0025602 | 0.0025536 | 0.0061 | 0.0092 | 2.9935
3921 | - | - | 13 | 0.82017 | 70.84 | 83.0854 | 25.3232 | 19.9832 | 19.9832 | 8.2741 | 0.0025536 | 0.0025471 | 0.0092 | 0.0011 | 2.0153
3931 | - | - | 13 | 0.82017 | 70.84 | 83.089 | 25.3243 | 19.9843 | 19.9843 | 8.2766 | 0.0025471 | 0.0025407 | 0.0011 | 0.0042 | 1.0433 | 0.020147 | 0.019749 | -0.0017 | 0.0037 | 0.052841
3941 | - | - | 13 | 0.82017 | 70.84 | 83.1028 | 25.3285 | 19.9885 | 19.9885 | 8.2792 | 0.0025407 | 0.0025342 | 0.0042 | 0.0082 | 2.4454
3951 | - | - | 13 | 0.82017 | 70.84 | 83.1297 | 25.3367 | 19.9967 | 19.9967 | 8.2817 | 0.0025342 | 0.0025278 | 0.0082 | 0.0046 | 2.5268
3961 | - | - | 13 | 0.82017 | 70.84 | 83.1448 | 25.3413 | 20.0013 | 20.0013 | 8.2843 | 0.0025278 | 0.0025214 | 0.0046 | -0.0043 | 0.054965
3971 | - | - | 13 | 0.82017 | 70.84 | 83.1307 | 25.337 | 19.997 | 19.997 | 8.2868 | 0.0025214 | 0.0025151 | -0.0043 | 0.0042 | -0.015605
3981 | - | - | 13 | 0.82017 | 70.84 | 83.1445 | 25.3412 | 20.0012 | 20.0012 | 8.2893 | 0.0025151 | 0.0025088 | 0.0042 | 0.0017 | 1.1731
3991 | - | - | 13 | 0.82017 | 70.84 | 83.1501 | 25.3429 | 20.0029 | 20.0029 | 8.2918 | 0.0025088 | 0.0025025 | 0.0017 | -0.0218 | -4.0227
4001 | - | - | 13 | 0.82017 | 70.84 | 83.0785 | 25.3211 | 19.9811 | 19.9811 | 8.2943 | 0.0025025 | 0.0024963 | -0.0218 | 0.0015 | -4.0494
4011 | - | - | 13 | 0.82017 | 70.84 | 83.0835 | 25.3226 | 19.9826 | 19.9826 | 8.2968 | 0.0024963 | 0.00249 | 0.0015 | -0.009 | -1.5094 | 0.019749 | 0.019366 | 0.0037 | 0.0208 | 0.63502
4021 | - | - | 13 | 0.82017 | 70.84 | 83.0539 | 25.3136 | 19.9736 | 19.9736 | 8.2993 | 0.00249 | 0.0024839 | -0.009 | 0.0092 | 0.04931
4031 | - | - | 13 | 0.82017 | 70.84 | 83.0841 | 25.3228 | 19.9828 | 19.9828 | 8.3018 | 0.0024839 | 0.0024777 | 0.0092 | -0.0065 | 0.53634
4041 | - | - | 13 | 0.82017 | 70.84 | 83.0628 | 25.3163 | 19.9763 | 19.9763 | 8.3042 | 0.0024777 | 0.0024716 | -0.0065 | 0.0039 | -0.52013
4051 | - | - | 13 | 0.82017 | 70.84 | 83.0756 | 25.3202 | 19.9802 | 19.9802 | 8.3067 | 0.0024716 | 0.0024655 | 0.0039 | 0.0108 | 2.9809
4061 | - | - | 13 | 0.82017 | 70.84 | 83.111 | 25.331 | 19.991 | 19.991 | 8.3092 | 0.0024655 | 0.0024594 | 0.0108 | 0.0038 | 2.961
4071 | - | - | 13 | 0.82017 | 70.84 | 83.1235 | 25.3348 | 19.9948 | 19.9948 | 8.3116 | 0.0024594 | 0.0024534 | 0.0038 | -0.003 | 0.15944
4081 | - | - | 13 | 0.82017 | 70.84 | 83.1136 | 25.3318 | 19.9918 | 19.9918 | 8.3141 | 0.0024534 | 0.0024474 | -0.003 | -0.0055 | -1.7357
4091 | - | - | 13 | 0.82017 | 70.84 | 83.0956 | 25.3263 | 19.9863 | 19.9863 | 8.3165 | 0.0024474 | 0.0024414 | -0.0055 | 0.0101 | 0.94873 | 0.019366 | 0.018998 | 0.0208 | 0.0113 | 0.83211
4101 | - | - | 13 | 0.82017 | 70.84 | 83.1287 | 25.3364 | 19.9964 | 19.9964 | 8.319 | 0.0024414 | 0.0024355 | 0.0101 | 0.0045 | 2.9909
4111 | - | - | 13 | 0.82017 | 70.84 | 83.1435 | 25.3409 | 20.0009 | 20.0009 | 8.3214 | 0.0024355 | 0.0024295 | 0.0045 | -0.0041 | 0.07792
4121 | - | - | 13 | 0.82017 | 70.84 | 83.13 | 25.3368 | 19.9968 | 19.9968 | 8.3239 | 0.0024295 | 0.0024237 | -0.0041 | 0.0032 | -0.1818
4131 | - | - | 13 | 0.82017 | 70.84 | 83.1405 | 25.34 | 20 | 20 | 8.3263 | 0.0024237 | 0.0024178 | 0.0032 | 0.0027 | 1.2184
4141 | - | - | 13 | 0.82017 | 70.84 | 83.1494 | 25.3427 | 20.0027 | 20.0027 | 8.3287 | 0.0024178 | 0.002412 | 0.0027 | 0.0006 | 0.68222
4151 | - | - | 13 | 0.82017 | 70.84 | 83.1514 | 25.3433 | 20.0033 | 20.0033 | 8.3311 | 0.002412 | 0.0024062 | 0.0006 | 0.002 | 0.54033
4161 | - | - | 13 | 0.82017 | 70.84 | 83.1579 | 25.3453 | 20.0053 | 20.0053 | 8.3335 | 0.0024062 | 0.0024004 | 0.002 | 0.0018 | 0.79049
4171 | - | - | 13 | 0.82017 | 70.84 | 83.1638 | 25.3471 | 20.0071 | 20.0071 | 8.3359 | 0.0024004 | 0.0023946 | 0.0018 | -0.0106 | -1.8414 | 0.018998 | -2.3793 | 0.0113 | -7.35 | 0.57471
4181 | - | - | 13 | 0.82017 | 70.84 | 83.1291 | 25.3365 | 19.9965 | 19.9965 | 8.3383 | 0.0023946 | 0.0023889 | -0.0106 | 0.0048 | -1.2048
4191 | - | - | 13 | 0.82017 | 70.84 | 83.1448 | 25.3413 | 20.0013 | 20.0013 | 8.3407 | 0.0023889 | 0.0023832 | 0.0048 | -0.0009 | 0.8144
4201 | - | - | 13 | 0.82017 | 70.84 | 83.1419 | 25.3404 | 20.0004 | 20.0004 | 8.3431 | 0.0023832 | 0.0023776 | -0.0009 | 0.0071 | 1.3063
4211 | - | - | 13 | 0.82017 | 70.84 | 83.1651 | 25.3475 | 20.0075 | 20.0075 | 8.3455 | 0.0023776 | 0.0023719 | 0.0071 | 0.0019 | 1.8924
4221 | - | - | 13 | 0.82017 | 70.84 | 83.1714 | 25.3494 | 20.0094 | 20.0094 | 8.3478 | 0.0023719 | 0.0023663 | 0.0019 | 0.0008 | 0.56929
4231 | - | - | 13 | 0.82017 | 70.84 | 83.174 | 25.3502 | 20.0102 | 20.0102 | 8.3502 | 0.0023663 | 0.0023607 | 0.0008 | 0.0018 | 0.55053
4241 | - | - | 13 | 0.82017 | 70.84 | 83.1799 | 25.352 | 20.012 | 20.012 | 8.3526 | 0.0023607 | 0.0023552 | 0.0018 | 0.0064 | 1.7411
4251 | - | - | 13 | 0.82017 | 70.84 | 83.2009 | 25.3584 | 20.0184 | 20.0184 | 8.3549 | 0.0023552 | 0.0023496 | 0.0064 | 0.0053 | 2.4863 | -2.3793 | -2.0947 | -7.35 | -4.2246 | 2.5189
4261 | - | - | 13 | 0.82017 | 70.84 | 83.2183 | 25.3637 | 20.0237 | 20.0237 | 8.3573 | 0.0023496 | 0.0023441 | 0.0053 | -0.0006 | 0.99839
4271 | - | - | 13 | 0.82017 | 70.84 | 83.2163 | 25.3631 | 20.0231 | 20.0231 | 8.3596 | 0.0023441 | 0.0023386 | -0.0006 | -0.004 | -0.98403
4281 | - | - | 13 | 0.82017 | 70.84 | 83.2032 | 25.3591 | 20.0191 | 20.0191 | 8.3619 | 0.0023386 | 0.0023332 | -0.004 | 0.0007 | -0.70402
4291 | - | - | 13 | 0.82017 | 70.84 | 83.2055 | 25.3598 | 20.0198 | 20.0198 | 8.3643 | 0.0023332 | 0.0023277 | 0.0007 | 0.0047 | 1.1606
4301 | - | - | 13 | 0.82017 | 70.84 | 83.2209 | 25.3645 | 20.0245 | 20.0245 | 8.3666 | 0.0023277 | 0.0023223 | 0.0047 | 0.0225 | 5.8583
4311 | - | - | 13 | 0.82017 | 70.84 | 83.2947 | 25.387 | 20.047 | 20.047 | 8.3689 | 0.0023223 | #VALUE! | 0.0225 | -2.7657 | #VALUE!
4321 | 1 | 4321 | 0 | 0 | 0 | 74.2205 | 22.6213 | 17.2813 | 19.5587 | ln(t/t') | D(t/t')1 | D(t/t')2 | Ds1 | Ds2 | ds/d(t/t') | D(t/t')1 | D(t/t')2 | Ds1 | Ds2 | ds/d(t/t') (L-Spacing = 8) | d2s/d(t/t')2
4331 | 11 | 393.7273 | 0 | 0 | 0 | 59.0856 | 18.0084 | 12.6684 | 19.6419 | 5.9757 | #VALUE! | -0.64432 | -4.6129 | -1.4905 | #VALUE! | -2.0947 | -0.61283 | -4.2246 | -1.2 | 1.9714
4341 | 21 | 206.7143 | 0 | 0 | 0 | 54.1952 | 16.5179 | 11.1779 | 19.7095 | 5.3313 | -0.64432 | -0.38716 | -1.4905 | -0.7956 | 2.1519
4351 | 31 | 140.3548 | 0 | 0 | 0 | 51.5849 | 15.7223 | 10.3823 | 19.8463 | 4.9442 | -0.38716 | -0.27729 | -0.7956 | -0.5145 | 1.9387
4361 | 41 | 106.3659 | 0 | 0 | 0 | 49.8968 | 15.2078 | 9.8678 | 20.0363 | 4.6669 | -0.27729 | -0.21596 | -0.5145 | -0.3882 | 1.8229
4371 | 51 | 85.7059 | 0 | 0 | 0 | 48.6231 | 14.8196 | 9.4796 | 20.1772 | 4.4509 | -0.21596 | -0.17676 | -0.3882 | -0.3104 | 1.7747
4381 | 61 | 71.8197 | 0 | 0 | 0 | 47.6047 | 14.5092 | 9.1692 | 20.2817 | 4.2742 | -0.17676 | -0.14953 | -0.3104 | -0.2776 | 1.8105
4391 | 71 | 61.8451 | 0 | 0 | 0 | 46.6939 | 14.2316 | 8.8916 | 20.3429 | 4.1246 | -0.14953 | -0.12949 | -0.2776 | -0.2392 | 1.8515
4401 | 81 | 54.3333 | 0 | 0 | 0 | 45.9091 | 13.9924 | 8.6524 | 20.3994 | 3.9951 | -0.12949 | -0.11414 | -0.2392 | -0.2086 | 1.8368
4411 | 91 | 48.4725 | 0 | 0 | 0 | 45.2246 | 13.7838 | 8.4438 | 20.4456 | 3.881 | -0.11414 | -0.102 | -0.2086 | -0.1938 | 1.8659 | -0.61283 | -0.36613 | -1.2 | -0.7423 | 2.0015
4421 | 101 | 43.7723 | 0 | 0 | 0 | 44.5888 | 13.59 | 8.25 | 20.4754 | 3.779 | -0.102 | -0.09215 | -0.1938 | -0.1764 | 1.9075
4431 | 111 | 39.9189 | 0 | 0 | 0 | 44.01 | 13.4136 | 8.0736 | 20.5074 | 3.6869 | -0.09215 | -0.084006 | -0.1764 | -0.1616 | 1.9192
4441 | 121 | 36.7025 | 0 | 0 | 0 | 43.4798 | 13.252 | 7.912 | 20.5424 | 3.6028 | -0.084006 | -0.077158 | -0.1616 | -0.1511 | 1.9417
4451 | 131 | 33.9771 | 0 | 0 | 0 | 42.9841 | 13.1009 | 7.7609 | 20.5805 | 3.5257 | -0.077158 | -0.071318 | -0.1511 | -0.1386 | 1.9506
4461 | 141 | 31.6383 | 0 | 0 | 0 | 42.5293 | 12.9623 | 7.6223 | 20.9956 | 3.4544 | -0.071318 | -0.066281 | -0.1386 | -0.1394 | 2.0262
4471 | 151 | 29.6093 | 0 | 0 | 0 | 42.0719 | 12.8229 | 7.4829 | 21.106 | 3.3881 | -0.066281 | -0.06189 | -0.1394 | -0.127 | 2.0767
4481 | 161 | 27.8323 | 0 | 0 | 0 | 41.6552 | 12.6959 | 7.3559 | 21.1644 | 3.3262 | -0.06189 | -0.05803 | -0.127 | -0.1121 | 1.99
4491 | 171 | 26.2632 | 0 | 0 | 0 | 41.2874 | 12.5838 | 7.2438 | 21.2287 | 3.2682 | -0.05803 | -0.054609 | -0.1121 | -0.1116 | 1.9894 | -0.36613 | -0.25932 | -0.7423 | -0.5117 | 1.9957
4501 | 181 | 24.8674 | 0 | 0 | 0 | 40.9213 | 12.4722 | 7.1322 | 21.2612 | 3.2136 | -0.054609 | -0.051557 | -0.1116 | -0.103 | 2.02
4511 | 191 | 23.6178 | 0 | 0 | 0 | 40.5833 | 12.3692 | 7.0292 | 21.291 | 3.162 | -0.051557 | -0.048817 | -0.103 | -0.1052 | 2.0785
4521 | 201 | 22.4925 | 0 | 0 | 0 | 40.2382 | 12.264 | 6.924 | 21.3209 | 3.1132 | -0.048817 | -0.046344 | -0.1052 | -0.0934 | 2.0834
4531 | 211 | 21.4739 | 0 | 0 | 0 | 39.9317 | 12.1706 | 6.8306 | 21.3601 | 3.0668 | -0.046344 | -0.0441 | -0.0934 | -0.086 | 1.9819
4541 | 221 | 20.5475 | 0 | 0 | 0 | 39.6496 | 12.0846 | 6.7446 | 21.3885 | 3.0227 | -0.0441 | -0.042055 | -0.086 | -0.0863 | 2.0023
4551 | 231 | 19.7013 | 0 | 0 | 0 | 39.3664 | 11.9983 | 6.6583 | 21.4175 | 2.9807 | -0.042055 | -0.040184 | -0.0863 | -0.0776 | 1.9902
4561 | 241 | 18.9253 | 0 | 0 | 0 | 39.1118 | 11.9207 | 6.5807 | 21.4382 | 2.9405 | -0.040184 | -0.038466 | -0.0776 | -0.0792 | 1.9964
4571 | 251 | 18.2112 | 0 | 0 | 0 | 38.852 | 11.8415 | 6.5015 | 21.4525 | 2.902 | -0.038466 | -0.036882 | -0.0792 | -0.0709 | 1.9892 | -0.25932 | -0.19942 | -0.5117 | -0.3918 | 1.9684
4581 | 261 | 17.5517 | 0 | 0 | 0 | 38.6193 | 11.7706 | 6.4306 | 21.4769 | 2.8652 | -0.036882 | -0.035418 | -0.0709 | -0.0705 | 1.9571
4591 | 271 | 16.941 | 0 | 0 | 0 | 38.388 | 11.7001 | 6.3601 | 21.4981 | 2.8297 | -0.035418 | -0.03406 | -0.0705 | -0.0704 | 2.0295
4601 | 281 | 16.3737 | 0 | 0 | 0 | 38.157 | 11.6297 | 6.2897 | 21.5163 | 2.7957 | -0.03406 | -0.032798 | -0.0704 | -0.0636 | 2.0018
4611 | 291 | 15.8454 | 0 | 0 | 0 | 37.9484 | 11.5661 | 6.2261 | 21.5336 | 2.7629 | -0.032798 | -0.031621 | -0.0636 | -0.0611 | 1.9357
4621 | 301 | 15.3522 | 0 | 0 | 0 | 37.7479 | 11.505 | 6.165 | 21.5389 | 2.7313 | -0.031621 | -0.030521 | -0.0611 | -0.0611 | 1.9677
4631 | 311 | 14.8907 | 0 | 0 | 0 | 37.5474 | 11.4439 | 6.1039 | 21.5583 | 2.7007 | -0.030521 | -0.029491 | -0.0611 | -0.0553 | 1.9374
4641 | 321 | 14.4579 | 0 | 0 | 0 | 37.366 | 11.3886 | 6.0486 | 21.5811 | 2.6712 | -0.029491 | -0.028525 | -0.0553 | -0.0588 | 1.9698
4651 | 331 | 14.0514 | 0 | 0 | 0 | 37.1731 | 11.3298 | 5.9898 | 21.5885 | 2.6427 | -0.028525 | -0.027616 | -0.0588 | -0.0533 | 1.9946 | -0.19942 | -0.16108 | -0.3918 | -0.3219 | 1.9833
4661 | 341 | 13.6686 | 0 | 0 | 0 | 36.9982 | 11.2765 | 5.9365 | 21.5724 | 2.6151 | -0.027616 | -0.026761 | -0.0533 | -0.0527 | 1.95
4671 | 351 | 13.3077 | 0 | 0 | 0 | 36.8253 | 11.2238 | 5.8838 | 21.6026 | 2.5883 | -0.026761 | -0.025953 | -0.0527 | -0.053 | 2.0063
4681 | 361 | 12.9668 | 0 | 0 | 0 | 36.6514 | 11.1708 | 5.8308 | 21.5993 | 2.5624 | -0.025953 | -0.02519 | -0.053 | -0.049 | 1.993
4691 | 371 | 12.6442 | 0 | 0 | 0 | 36.4906 | 11.1218 | 5.7818 | 21.6131 | 2.5372 | -0.02519 | -0.024468 | -0.049 | -0.0477 | 1.9474
4701 | 381 | 12.3386 | 0 | 0 | 0 | 36.3341 | 11.0741 | 5.7341 | 21.6123 | 2.5127 | -0.024468 | -0.023783 | -0.0477 | -0.0479 | 1.9822
4711 | 391 | 12.0486 | 0 | 0 | 0 | 36.177 | 11.0262 | 5.6862 | 21.6202 | 2.4889 | -0.023783 | -0.023133 | -0.0479 | -0.0431 | 1.9375
4721 | 401 | 11.7731 | 0 | 0 | 0 | 36.0356 | 10.9831 | 5.6431 | 21.6164 | 2.4658 | -0.023133 | -0.022516 | -0.0431 | -0.0451 | 1.934
4731 | 411 | 11.5109 | 0 | 0 | 0 | 35.8876 | 10.938 | 5.598 | 21.6274 | 2.4433 | -0.022516 | -0.021928 | -0.0451 | -0.0452 | 2.0325 | -0.16108 | -0.13445 | -0.3219 | -0.2766 | 2.0304
4741 | 421 | 11.2613 | 0 | 0 | 0 | 35.7393 | 10.8928 | 5.5528 | 21.6296 | 2.4214 | -0.021928 | -0.021368 | -0.0452 | -0.0403 | 1.9725
4751 | 431 | 11.0232 | 0 | 0 | 0 | 35.6071 | 10.8525 | 5.5125 | 21.6411 | 2.4 | -0.021368 | -0.020834 | -0.0403 | -0.0427 | 1.9688
4761 | 441 | 10.7959 | 0 | 0 | 0 | 35.467 | 10.8098 | 5.4698 | 21.6392 | 2.3792 | -0.020834 | -0.020324 | -0.0427 | -0.0462 | 2.1627
4771 | 451 | 10.5787 | 0 | 0 | 0 | 35.3154 | 10.7636 | 5.4236 | 21.633 | 2.3588 | -0.020324 | -0.019837 | -0.0462 | -0.037 | 2.0667
4781 | 461 | 10.3709 | 0 | 0 | 0 | 35.194 | 10.7266 | 5.3866 | 21.6418 | 2.339 | -0.019837 | -0.019371 | -0.037 | -0.0379 | 1.9114
4791 | 471 | 10.172 | 0 | 0 | 0 | 35.0696 | 10.6887 | 5.3487 | 21.6434 | 2.3196 | -0.019371 | -0.018924 | -0.0379 | -0.0383 | 1.9906
4801 | 481 | 9.9813 | 0 | 0 | 0 | 34.944 | 10.6504 | 5.3104 | 21.6533 | 2.3007 | -0.018924 | -0.018496 | -0.0383 | -0.0343 | 1.9382
4811 | 491 | 9.7984 | 0 | 0 | 0 | 34.8314 | 10.6161 | 5.2761 | 21.6591 | 2.2822 | -0.018496 | -0.018086 | -0.0343 | -0.0368 | 1.9456 | -0.13445 | -0.1149 | -0.2766 | -0.2284 | 2.0198
4821 | 501 | 9.6228 | 0 | 0 | 0 | 34.7107 | 10.5793 | 5.2393 | 21.6554 | 2.2641 | -0.018086 | -0.017691 | -0.0368 | -0.0354 | 2.0177
4831 | 511 | 9.454 | 0 | 0 | 0 | 34.5945 | 10.5439 | 5.2039 | 21.657 | 2.2464 | -0.017691 | -0.017313 | -0.0354 | -0.0356 | 2.0289
4841 | 521 | 9.2917 | 0 | 0 | 0 | 34.4777 | 10.5083 | 5.1683 | 21.6552 | 2.2291 | -0.017313 | -0.016948 | -0.0356 | -0.0369 | 2.1174
4851 | 531 | 9.1356 | 0 | 0 | 0 | 34.3567 | 10.4714 | 5.1314 | 21.6508 | 2.2122 | -0.016948 | -0.016598 | -0.0369 | -0.0328 | 2.0756
4861 | 541 | 8.9852 | 0 | 0 | 0 | 34.249 | 10.4386 | 5.0986 | 21.6691 | 2.1956 | -0.016598 | -0.01626 | -0.0328 | -0.032 | 1.972
4871 | 551 | 8.8403 | 0 | 0 | 0 | 34.1441 | 10.4066 | 5.0666 | 21.6654 | 2.1793 | -0.01626 | -0.015935 | -0.032 | -0.0346 | 2.0707
4881 | 561 | 8.7005 | 0 | 0 | 0 | 34.0305 | 10.372 | 5.032 | 21.6547 | 2.1634 | -0.015935 | -0.015622 | -0.0346 | -0.0325 | 2.1254
4891 | 571 | 8.5657 | 0 | 0 | 0 | 33.9239 | 10.3395 | 4.9995 | 21.6594 | 2.1478 | -0.015622 | -0.015319 | -0.0325 | -0.0297 | 2.0089 | -0.1149 | -0.099939 | -0.2284 | -0.1889 | 1.9356
4901 | 581 | 8.4355 | 0 | 0 | 0 | 33.8265 | 10.3098 | 4.9698 | 21.6654 | 2.1324 | -0.015319 | -0.015027 | -0.0297 | -0.0314 | 2.0149
4911 | 591 | 8.3096 | 0 | 0 | 0 | 33.7234 | 10.2784 | 4.9384 | 21.6636 | 2.1174 | -0.015027 | -0.014745 | -0.0314 | -0.0306 | 2.0824
4921 | 601 | 8.188 | 0 | 0 | 0 | 33.623 | 10.2478 | 4.9078 | 21.6576 | 2.1027 | -0.014745 | -0.014472 | -0.0306 | -0.0268 | 1.9625
4931 | 611 | 8.0704 | 0 | 0 | 0 | 33.5351 | 10.221 | 4.881 | 21.6773 | 2.0882 | -0.014472 | -0.014208 | -0.0268 | -0.0261 | 1.8443
4941 | 621 | 7.9565 | 0 | 0 | 0 | 33.4495 | 10.1949 | 4.8549 | 21.6792 | 2.074 | -0.014208 | -0.013953 | -0.0261 | -0.0312 | 2.0383
4951 | 631 | 7.8463 | 0 | 0 | 0 | 33.3471 | 10.1637 | 4.8237 | 21.6735 | 2.06 | -0.013953 | -0.013706 | -0.0312 | -0.0263 | 2.0761
4961 | 641 | 7.7395 | 0 | 0 | 0 | 33.2608 | 10.1374 | 4.7974 | 21.6774 | 2.0463 | -0.013706 | -0.013466 | -0.0263 | -0.0263 | 1.9361
4971 | 651 | 7.6359 | 0 | 0 | 0 | 33.1745 | 10.1111 | 4.7711 | 21.6826 | 2.0329 | -0.013466 | -0.013235 | -0.0263 | -0.0291 | 2.077 | -0.099939 | -0.08814 | -0.1889 | -0.1656 | 1.8841
4981 | 661 | 7.5356 | 0 | 0 | 0 | 33.079 | 10.082 | 4.742 | 21.6848 | 2.0196 | -0.013235 | -0.01301 | -0.0291 | -0.0265 | 2.1172
4991 | 671 | 7.4382 | 0 | 0 | 0 | 32.9921 | 10.0555 | 4.7155 | 21.6857 | 2.0066 | -0.01301 | -0.012792 | -0.0265 | -0.0254 | 2.0111
5001 | 681 | 7.3436 | 0 | 0 | 0 | 32.9088 | 10.0301 | 4.6901 | 21.6921 | 1.9938 | -0.012792 | -0.01258 | -0.0254 | -0.0198 | 1.7781
5011 | 691 | 7.2518 | 0 | 0 | 0 | 32.8438 | 10.0103 | 4.6703 | 21.6979 | 1.9813 | -0.01258 | -0.012374 | -0.0198 | -0.0246 | 1.7827
5021 | 701 | 7.1626 | 0 | 0 | 0 | 32.7631 | 9.9857 | 4.6457 | 21.7016 | 1.9689 | -0.012374 | -0.012175 | -0.0246 | -0.0218 | 1.8885
5031 | 711 | 7.0759 | 0 | 0 | 0 | 32.6916 | 9.9639 | 4.6239 | 21.7077 | 1.9567 | -0.012175 | -0.011981 | -0.0218 | -0.0195 | 1.7084
5041 | 721 | 6.9917 | 0 | 0 | 0 | 32.6276 | 9.9444 | 4.6044 | 21.7223 | 1.9447 | -0.011981 | -0.011793 | -0.0195 | -0.0222 | 1.7561
5051 | 731 | 6.9097 | 0 | 0 | 0 | 32.5547 | 9.9222 | 4.5822 | 21.7246 | 1.9329 | -0.011793 | -0.011609 | -0.0222 | -0.0238 | 1.967 | -0.08814 | -0.078605 | -0.1656 | -0.1312 | 1.768
5061 | 741 | 6.83 | 0 | 0 | 0 | 32.4767 | 9.8984 | 4.5584 | 21.7293 | 1.9213 | -0.011609 | -0.011431 | -0.0238 | -0.0183 | 1.8238
5071 | 751 | 6.7523 | 0 | 0 | 0 | 32.4166 | 9.8801 | 4.5401 | 21.7466 | 1.9099 | -0.011431 | -0.011258 | -0.0183 | -0.0277 | 2.034
5081 | 761 | 6.6767 | 0 | 0 | 0 | 32.3257 | 9.8524 | 4.5124 | 21.7451 | 1.8986 | -0.011258 | -0.011089 | -0.0277 | -0.0197 | 2.116
5091 | 771 | 6.6031 | 0 | 0 | 0 | 32.2611 | 9.8327 | 4.4927 | 21.7545 | 1.8875 | -0.011089 | -0.010924 | -0.0197 | -0.0225 | 1.9191
5101 | 781 | 6.5314 | 0 | 0 | 0 | 32.1873 | 9.8102 | 4.4702 | 21.7593 | 1.8766 | -0.010924 | -0.010764 | -0.0225 | -0.0167 | 1.8036
5111 | 791 | 6.4614 | 0 | 0 | 0 | 32.1325 | 9.7935 | 4.4535 | 21.7719 | 1.8659 | -0.010764 | -0.010608 | -0.0167 | -0.0171 | 1.5819
5121 | 801 | 6.3933 | 0 | 0 | 0 | 32.0764 | 9.7764 | 4.4364 | 21.7881 | 1.8552 | -0.010608 | -0.010456 | -0.0171 | -0.0198 | 1.7538
5131 | 811 | 6.3268 | 0 | 0 | 0 | 32.0114 | 9.7566 | 4.4166 | 21.7899 | 1.8448 | -0.010456 | -0.010308 | -0.0198 | -0.0172 | 1.7803 | -0.078605 | -0.070747 | -0.1312 | -0.1236 | 1.7101
5141 | 821 | 6.2619 | 0 | 0 | 0 | 31.955 | 9.7394 | 4.3994 | 21.7888 | 1.8345 | -0.010308 | -0.010163 | -0.0172 | -0.012 | 1.4229
5151 | 831 | 6.1986 | 0 | 0 | 0 | 31.9156 | 9.7274 | 4.3874 | 21.7812 | 1.8243 | -0.010163 | -0.010022 | -0.012 | -0.0272 | 1.9527
5161 | 841 | 6.1367 | 0 | 0 | 0 | 31.8264 | 9.7002 | 4.3602 | 21.7774 | 1.8143 | -0.010022 | -0.0098847 | -0.0272 | -0.012 | 1.9588
5171 | 851 | 6.0764 | 0 | 0 | 0 | 31.787 | 9.6882 | 4.3482 | 21.7851 | 1.8044 | -0.0098847 | -0.0097504 | -0.012 | -0.0164 | 1.4496
5181 | 861 | 6.0174 | 0 | 0 | 0 | 31.7332 | 9.6718 | 4.3318 | 21.79 | 1.7947 | -0.0097504 | -0.0096192 | -0.0164 | -0.0138 | 1.5575
5191 | 871 | 5.9598 | 0 | 0 | 0 | 31.6879 | 9.658 | 4.318 | 21.8017 | 1.785 | -0.0096192 | -0.0094911 | -0.0138 | -0.016 | 1.5611
5201 | 881 | 5.9035 | 0 | 0 | 0 | 31.6354 | 9.642 | 4.302 | 21.8147 | 1.7755 | -0.0094911 | -0.0093659 | -0.016 | -0.0166 | 1.7294
5211 | 891 | 5.8485 | 0 | 0 | 0 | 31.5809 | 9.6254 | 4.2854 | 21.8145 | 1.7662 | -0.0093659 | -0.0092437 | -0.0166 | -0.016 | 1.7515 | -0.070747 | -0.064164 | -0.1236 | -0.1199 | 1.8108
5221 | 901 | 5.7947 | 0 | 0 | 0 | 31.5284 | 9.6094 | 4.2694 | 21.8276 | 1.7569 | -0.0092437 | -0.0091241 | -0.016 | -0.0176 | 1.8306
5231 | 911 | 5.742 | 0 | 0 | 0 | 31.4707 | 9.5918 | 4.2518 | 21.8241 | 1.7478 | -0.0091241 | -0.0090073 | -0.0176 | -0.0149 | 1.7907
5241 | 921 | 5.6906 | 0 | 0 | 0 | 31.4218 | 9.5769 | 4.2369 | 21.839 | 1.7388 | -0.0090073 | -0.008893 | -0.0149 | -0.0146 | 1.6479
5251 | 931 | 5.6402 | 0 | 0 | 0 | 31.3739 | 9.5623 | 4.2223 | 21.8465 | 1.7299 | -0.008893 | -0.0087813 | -0.0146 | -0.0151 | 1.6809
5261 | 941 | 5.5909 | 0 | 0 | 0 | 31.3244 | 9.5472 | 4.2072 | 21.8479 | 1.7211 | -0.0087813 | -0.0086719 | -0.0151 | -0.0188 | 1.9451
5271 | 951 | 5.5426 | 0 | 0 | 0 | 31.2627 | 9.5284 | 4.1884 | 21.8495 | 1.7125 | -0.0086719 | -0.008565 | -0.0188 | -0.0123 | 1.7997
5281 | 961 | 5.4953 | 0 | 0 | 0 | 31.2223 | 9.5161 | 4.1761 | 21.8431 | 1.7039 | -0.008565 | -0.0084603 | -0.0123 | -0.0143 | 1.5639
5291 | 971 | 5.449 | 0 | 0 | 0 | 31.1754 | 9.5018 | 4.1618 | 21.8307 | 1.6954 | -0.0084603 | -0.0083578 | -0.0143 | -0.0173 | 1.8812 | -0.064164 | -0.058575 | -0.1199 | -0.1151 | 1.919
5301 | 981 | 5.4037 | 0 | 0 | 0 | 31.1186 | 9.4845 | 4.1445 | 21.8366 | 1.6871 | -0.0083578 | -0.0082574 | -0.0173 | -0.0137 | 1.8633
5311 | 991 | 5.3592 | 0 | 0 | 0 | 31.0737 | 9.4708 | 4.1308 | 21.8378 | 1.6788 | -0.0082574 | -0.0081591 | -0.0137 | -0.0145 | 1.7185
5321 | 1001 | 5.3157 | 0 | 0 | 0 | 31.0261 | 9.4563 | 4.1163 | 21.8457 | 1.6707 | -0.0081591 | -0.0080629 | -0.0145 | -0.0157 | 1.8627
5331 | 1011 | 5.273 | 0 | 0 | 0 | 30.9746 | 9.4406 | 4.1006 | 21.8508 | 1.6626 | -0.0080629 | -0.0079685 | -0.0157 | -0.0172 | 2.0535
5341 | 1021 | 5.2311 | 0 | 0 | 0 | 30.9182 | 9.4234 | 4.0834 | 21.8475 | 1.6546 | -0.0079685 | -0.0078761 | -0.0172 | -0.0119 | 1.8328
5351 | 1031 | 5.1901 | 0 | 0 | 0 | 30.8791 | 9.4115 | 4.0715 | 21.8504 | 1.6468 | -0.0078761 | -0.0077855 | -0.0119 | -0.0115 | 1.4939
5361 | 1041 | 5.1499 | 0 | 0 | 0 | 30.8414 | 9.4 | 4.06 | 21.8517 | 1.639 | -0.0077855 | -0.0076967 | -0.0115 | -0.0181 | 1.9169
5371 | 1051 | 5.1104 | 0 | 0 | 0 | 30.782 | 9.3819 | 4.0419 | 21.8498 | 1.6313 | -0.0076967 | -0.0076096 | -0.0181 | -0.0135 | 2.0612 | -0.058575 | -0.053775 | -0.1151 | -0.1189 | 2.0933
5381 | 1061 | 5.0716 | 0 | 0 | 0 | 30.7377 | 9.3684 | 4.0284 | 21.861 | 1.6237 | -0.0076096 | -0.0075243 | -0.0135 | -0.0117 | 1.6639
5391 | 1071 | 5.0336 | 0 | 0 | 0 | 30.6993 | 9.3567 | 4.0167 | 21.8672 | 1.6161 | -0.0075243 | -0.0074405 | -0.0117 | -0.0194 | 2.0841
5401 | 1081 | 4.9963 | 0 | 0 | 0 | 30.6357 | 9.3373 | 3.9973 | 21.8665 | 1.6087 | -0.0074405 | -0.0073584 | -0.0194 | -0.0155 | 2.3555
5411 | 1091 | 4.9597 | 0 | 0 | 0 | 30.5848 | 9.3218 | 3.9818 | 21.8648 | 1.6013 | -0.0073584 | -0.0072778 | -0.0155 | -0.0149 | 2.0767
5421 | 1101 | 4.9237 | 0 | 0 | 0 | 30.5359 | 9.3069 | 3.9669 | 21.8602 | 1.5941 | -0.0072778 | -0.0071987 | -0.0149 | -0.0129 | 1.919
5431 | 1111 | 4.8884 | 0 | 0 | 0 | 30.4936 | 9.294 | 3.954 | 21.8665 | 1.5869 | -0.0071987 | -0.007121 | -0.0129 | -0.015 | 1.9501
5441 | 1121 | 4.8537 | 0 | 0 | 0 | 30.4444 | 9.279 | 3.939 | 21.8621 | 1.5797 | -0.007121 | -0.0070448 | -0.015 | -0.0122 | 1.9181
5451 | 1131 | 4.8196 | 0 | 0 | 0 | 30.4044 | 9.2668 | 3.9268 | 21.868 | 1.5727 | -0.0070448 | -0.00697 | -0.0122 | -0.0168 | 2.0729 | -0.053775 | -0.04961 | -0.1189 | -0.1063 | 2.1755
5461 | 1141 | 4.7862 | 0 | 0 | 0 | 30.3493 | 9.25 | 3.91 | 21.8803 | 1.5657 | -0.00697 | -0.0068966 | -0.0168 | -0.0151 | 2.2993
5471 | 1151 | 4.7533 | 0 | 0 | 0 | 30.2997 | 9.2349 | 3.8949 | 21.8762 | 1.5588 | -0.0068966 | -0.0068244 | -0.0151 | -0.0117 | 1.9507
5481 | 1161 | 4.7209 | 0 | 0 | 0 | 30.2613 | 9.2232 | 3.8832 | 21.8799 | 1.552 | -0.0068244 | -0.0067536 | -0.0117 | -0.0167 | 2.0956
5491 | 1171 | 4.6892 | 0 | 0 | 0 | 30.2065 | 9.2065 | 3.8665 | 21.8788 | 1.5453 | -0.0067536 | -0.0066839 | -0.0167 | -0.0132 | 2.2225
5501 | 1181 | 4.6579 | 0 | 0 | 0 | 30.1632 | 9.1933 | 3.8533 | 21.889 | 1.5386 | -0.0066839 | -0.0066156 | -0.0132 | -0.0162 | 2.213
5511 | 1191 | 4.6272 | 0 | 0 | 0 | 30.1101 | 9.1771 | 3.8371 | 21.8899 | 1.532 | -0.0066156 | -0.0065483 | -0.0162 | -0.0136 | 2.2619
5521 | 1201 | 4.597 | 0 | 0 | 0 | 30.0654 | 9.1635 | 3.8235 | 21.8809 | 1.5254 | -0.0065483 | -0.0064823 | -0.0136 | -0.0156 | 2.2425
5531 | 1211 | 4.5673 | 0 | 0 | 0 | 30.0143 | 9.1479 | 3.8079 | 21.8808 | 1.5189 | -0.0064823 | -0.0064174 | -0.0156 | -0.0122 | 2.1526 | -0.04961 | -0.045966 | -0.1063 | -0.0915 | 2.0637
5541 | 1221 | 4.5381 | 0 | 0 | 0 | 29.9742 | 9.1357 | 3.7957 | 21.8852 | 1.5125 | -0.0064174 | -0.0063536 | -0.0122 | -0.0162 | 2.227
5551 | 1231 | 4.5093 | 0 | 0 | 0 | 29.9211 | 9.1195 | 3.7795 | 21.8761 | 1.5062 | -0.0063536 | -0.0062908 | -0.0162 | -0.0115 | 2.1871
5561 | 1241 | 4.4811 | 0 | 0 | 0 | 29.8833 | 9.108 | 3.768 | 21.8798 | 1.4999 | -0.0062908 | -0.0062291 | -0.0115 | -0.0174 | 2.3131
5571 | 1251 | 4.4532 | 0 | 0 | 0 | 29.8263 | 9.0906 | 3.7506 | 21.8798 | 1.4936 | -0.0062291 | -0.0061684 | -0.0174 | -0.0077 | 2.017
5581 | 1261 | 4.4259 | 0 | 0 | 0 | 29.801 | 9.0829 | 3.7429 | 21.8905 | 1.4875 | -0.0061684 | -0.0061087 | -0.0077 | -0.0134 | 1.7232
5591 | 1271 | 4.3989 | 0 | 0 | 0 | 29.757 | 9.0695 | 3.7295 | 21.8819 | 1.4814 | -0.0061087 | -0.00605 | -0.0134 | -0.0112 | 2.0216
5601 | 1281 | 4.3724 | 0 | 0 | 0 | 29.7203 | 9.0583 | 3.7183 | 21.8845 | 1.4753 | -0.00605 | -0.0059923 | -0.0112 | -0.0167 | 2.3213
5611 | 1291 | 4.3462 | 0 | 0 | 0 | 29.6655 | 9.0416 | 3.7016 | 21.8814 | 1.4693 | -0.0059923 | -0.0059355 | -0.0167 | -0.0109 | 2.3094 | -0.045966 | -0.042753 | -0.0915 | -0.0767 | 1.8887
5621 | 1301 | 4.3205 | 0 | 0 | 0 | 29.6297 | 9.0307 | 3.6907 | 21.8775 | 1.4634 | -0.0059355 | -0.0058795 | -0.0109 | -0.0135 | 2.0673
5631 | 1311 | 4.2952 | 0 | 0 | 0 | 29.5854 | 9.0172 | 3.6772 | 21.8745 | 1.4575 | -0.0058795 | -0.0058245 | -0.0135 | -0.0118 | 2.1604
5641 | 1321 | 4.2702 | 0 | 0 | 0 | 29.5467 | 9.0054 | 3.6654 | 21.8782 | 1.4517 | -0.0058245 | -0.0057703 | -0.0118 | -0.0126 | 2.1051
5651 | 1331 | 4.2457 | 0 | 0 | 0 | 29.5054 | 8.9928 | 3.6528 | 21.8698 | 1.4459 | -0.0057703 | -0.005717 | -0.0126 | -0.0113 | 2.0796
5661 | 1341 | 4.2215 | 0 | 0 | 0 | 29.4683 | 8.9815 | 3.6415 | 21.8809 | 1.4402 | -0.005717 | -0.0056645 | -0.0113 | -0.0131 | 2.1454
5671 | 1351 | 4.1976 | 0 | 0 | 0 | 29.4253 | 8.9684 | 3.6284 | 21.8754 | 1.4345 | -0.0056645 | -0.0056129 | -0.0131 | -0.013 | 2.3144
5681 | 1361 | 4.1741 | 0 | 0 | 0 | 29.3827 | 8.9554 | 3.6154 | 21.8932 | 1.4289 | -0.0056129 | -0.005562 | -0.013 | -0.0053 | 1.6314
5691 | 1371 | 4.151 | 0 | 0 | 0 | 29.3653 | 8.9501 | 3.6101 | 21.9118 | 1.4233 | -0.005562 | -0.0055119 | -0.0053 | -0.0133 | 1.6862 | -0.042753 | -0.039901 | -0.0767 | -0.0544 | 1.5713
5701 | 1381 | 4.1282 | 0 | 0 | 0 | 29.3216 | 8.9368 | 3.5968 | 21.913 | 1.4178 | -0.0055119 | -0.0054625 | -0.0133 | -0.0101 | 2.1297
5711 | 1391 | 4.1057 | 0 | 0 | 0 | 29.2885 | 8.9267 | 3.5867 | 21.9098 | 1.4124 | -0.0054625 | -0.0054139 | -0.0101 | -0.0079 | 1.6532
5721 | 1401 | 4.0835 | 0 | 0 | 0 | 29.2626 | 8.9188 | 3.5788 | 21.9193 | 1.407 | -0.0054139 | -0.005366 | -0.0079 | -0.0142 | 2.0554
5731 | 1411 | 4.0617 | 0 | 0 | 0 | 29.216 | 8.9046 | 3.5646 | 21.9076 | 1.4016 | -0.005366 | -0.0053188 | -0.0142 | -0.0093 | 2.1954
5741 | 1421 | 4.0401 | 0 | 0 | 0 | 29.1855 | 8.8953 | 3.5553 | 21.9065 | 1.3963 | -0.0053188 | -0.0052723 | -0.0093 | -0.0053 | 1.3753
5751 | 1431 | 4.0189 | 0 | 0 | 0 | 29.1681 | 8.89 | 3.55 | 21.9177 | 1.391 | -0.0052723 | -0.0052265 | -0.0053 | -0.0085 | 1.3171
5761 | 1441 | 3.9979 | 0 | 0 | 0 | 29.1402 | 8.8815 | 3.5415 | 21.9163 | 1.3858 | -0.0052265 | -0.0051814 | -0.0085 | -0.0081 | 1.5947
5771 | 1451 | 3.9773 | 0 | 0 | 0 | 29.1136 | 8.8734 | 3.5334 | 21.9293 | 1.3806 | -0.0051814 | -0.0051369 | -0.0081 | -0.005 | 1.2671 | -0.039901 | -0.037354 | -0.0544 | -0.061 | 1.5027
5781 | 1461 | 3.9569 | 0 | 0 | 0 | 29.0972 | 8.8684 | 3.5284 | 21.9392 | 1.3755 | -0.0051369 | -0.005093 | -0.005 | -0.0118 | 1.648
5791 | 1471 | 3.9368 | 0 | 0 | 0 | 29.0585 | 8.8566 | 3.5166 | 21.9446 | 1.3704 | -0.005093 | -0.0050498 | -0.0118 | -0.0094 | 2.0882
5801 | 1481 | 3.9169 | 0 | 0 | 0 | 29.0277 | 8.8472 | 3.5072 | 21.9566 | 1.3653 | -0.0050498 | -0.0050071 | -0.0094 | -0.0105 | 1.9797
5811 | 1491 | 3.8974 | 0 | 0 | 0 | 28.9932 | 8.8367 | 3.4967 | 21.956 | 1.3603 | -0.0050071 | -0.0049651 | -0.0105 | -0.0105 | 2.1059
5821 | 1501 | 3.8781 | 0 | 0 | 0 | 28.9588 | 8.8262 | 3.4862 | 21.9642 | 1.3553 | -0.0049651 | -0.0049237 | -0.0105 | 0.0023 | 0.8184
5831 | 1511 | 3.859 | 0 | 0 | 0 | 28.9663 | 8.8285 | 3.4885 | 21.9766 | 1.3504 | -0.0049237 | -0.0048828 | 0.0023 | -0.0063 | 0.41521
5841 | 1521 | 3.8402 | 0 | 0 | 0 | 28.9456 | 8.8222 | 3.4822 | 21.972 | 1.3455 | -0.0048828 | -0.0048425 | -0.0063 | -0.0032 | 0.97422
5851 | 1531 | 3.8217 | 0 | 0 | 0 | 28.9351 | 8.819 | 3.479 | 21.9819 | 1.3407 | -0.0048425 | -0.0048028 | -0.0032 | -0.0051 | 0.86217 | -0.037354 | -0.035067 | -0.061 | -0.0491 | 1.5129
5861 | 1541 | 3.8034 | 0 | 0 | 0 | 28.9184 | 8.8139 | 3.4739 | 21.9868 | 1.3359 | -0.0048028 | -0.0047636 | -0.0051 | 0.0016 | 0.36014
5871 | 1551 | 3.7853 | 0 | 0 | 0 | 28.9237 | 8.8155 | 3.4755 | 21.9903 | 1.3311 | -0.0047636 | -0.0047249 | 0.0016 | -0.0222 | 2.1916
5881 | 1561 | 3.7675 | 0 | 0 | 0 | 28.8508 | 8.7933 | 3.4533 | 21.9862 | 1.3264 | -0.0047249 | -0.0046868 | -0.0222 | -0.0084 | 3.2395
5891 | 1571 | 3.7498 | 0 | 0 | 0 | 28.8233 | 8.7849 | 3.4449 | 21.9961 | 1.3217 | -0.0046868 | -0.0046491 | -0.0084 | 0.0057 | 0.27704
5901 | 1581 | 3.7324 | 0 | 0 | 0 | 28.842 | 8.7906 | 3.4506 | 22.0068 | 1.3171 | -0.0046491 | -0.004612 | 0.0057 | -0.0068 | 0.1296
5911 | 1591 | 3.7153 | 0 | 0 | 0 | 28.8196 | 8.7838 | 3.4438 | 22.0004 | 1.3125 | -0.004612 | -0.0045754 | -0.0068 | -0.0133 | 2.1935
5921 | 1601 | 3.6983 | 0 | 0 | 0 | 28.776 | 8.7705 | 3.4305 | 21.9993 | 1.3079 | -0.0045754 | -0.0045392 | -0.0133 | -0.0125 | 2.83
5931 | 1611 | 3.6816 | 0 | 0 | 0 | 28.735 | 8.758 | 3.418 | 21.996 | 1.3033 | -0.0045392 | -0.0045035 | -0.0125 | -0.0011 | 1.4941 | -0.035067 | -0.033003 | -0.0491 | -0.0698 | 1.7684
5941 | 1621 | 3.665 | 0 | 0 | 0 | 28.7314 | 8.7569 | 3.4169 | 22.031 | 1.2988 | -0.0045035 | -0.0044683 | -0.0011 | -0.0108 | 1.3349
5951 | 1631 | 3.6487 | 0 | 0 | 0 | 28.696 | 8.7461 | 3.4061 | 22.0451 | 1.2944 | -0.0044683 | -0.0044335 | -0.0108 | -0.0067 | 1.9624
5961 | 1641 | 3.6325 | 0 | 0 | 0 | 28.674 | 8.7394 | 3.3994 | 22.0497 | 1.2899 | -0.0044335 | -0.0043992 | -0.0067 | -0.009 | 1.7796
5971 | 1651 | 3.6166 | 0 | 0 | 0 | 28.6444 | 8.7304 | 3.3904 | 22.0408 | 1.2855 | -0.0043992 | -0.0043653 | -0.009 | -0.0049 | 1.5824
5981 | 1661 | 3.6008 | 0 | 0 | 0 | 28.6284 | 8.7255 | 3.3855 | 22.0433 | 1.2812 | -0.0043653 | -0.0043319 | -0.0049 | 0.0006 | 0.48956
5991 | 1671 | 3.5853 | 0 | 0 | 0 | 28.6303 | 8.7261 | 3.3861 | 22.0416 | 1.2768 | -0.0043319 | -0.0042988 | 0.0006 | -0.0094 | 1.0285
6001 | 1681 | 3.5699 | 0 | 0 | 0 | 28.5995 | 8.7167 | 3.3767 | 22.0433 | 1.2725 | -0.0042988 | -0.0042662 | -0.0094 | -0.0078 | 2.0068
6011 | 1691 | 3.5547 | 0 | 0 | 0 | 28.5739 | 8.7089 | 3.3689 | 22.0574 | 1.2683 | -0.0042662 | -0.004234 | -0.0078 | -0.0059 | 1.6101 | -0.033003 | -0.031133 | -0.0698 | -0.0788 | 2.3291
6021 | 1701 | 3.5397 | 0 | 0 | 0 | 28.5545 | 8.703 | 3.363 | 22.0484 | 1.264 | -0.004234 | -0.0042022 | -0.0059 | -0.0099 | 1.8765
6031 | 1711 | 3.5248 | 0 | 0 | 0 | 28.5221 | 8.6931 | 3.3531 | 22.0483 | 1.2598 | -0.0042022 | -0.0041708 | -0.0099 | -0.012 | 2.6175
6041 | 1721 | 3.5102 | 0 | 0 | 0 | 28.4827 | 8.6811 | 3.3411 | 22.0384 | 1.2557 | -0.0041708 | -0.0041398 | -0.012 | -0.0085 | 2.4637
6051 | 1731 | 3.4957 | 0 | 0 | 0 | 28.4548 | 8.6726 | 3.3326 | 22.0404 | 1.2515 | -0.0041398 | -0.0041091 | -0.0085 | -0.0076 | 1.951
6061 | 1741 | 3.4813 | 0 | 0 | 0 | 28.4299 | 8.665 | 3.325 | 22.0389 | 1.2474 | -0.0041091 | -0.0040789 | -0.0076 | -0.0072 | 1.8072
6071 | 1751 | 3.4672 | 0 | 0 | 0 | 28.4062 | 8.6578 | 3.3178 | 22.0379 | 1.2433 | -0.0040789 | -0.004049 | -0.0072 | -0.006 | 1.623
6081 | 1761 | 3.4532 | 0 | 0 | 0 | 28.3866 | 8.6518 | 3.3118 | 22.0503 | 1.2393 | -0.004049 | -0.0040194 | -0.006 | -0.0127 | 2.3238
6091 | 1771 | 3.4393 | 0 | 0 | 0 | 28.3449 | 8.6391 | 3.2991 | 22.0459 | 1.2353 | -0.0040194 | -0.0039902 | -0.0127 | -0.0048 | 2.1777 | -0.031133 | -0.029431 | -0.0788 | -0.0857 | 2.7268
6101 | 1781 | 3.4256 | 0 | 0 | 0 | 28.3291 | 8.6343 | 3.2943 | 22.0492 | 1.2313 | -0.0039902 | -0.0039614 | -0.0048 | -0.0148 | 2.4741
6111 | 1791 | 3.4121 | 0 | 0 | 0 | 28.2806 | 8.6195 | 3.2795 | 22.0391 | 1.2273 | -0.0039614 | -0.0039329 | -0.0148 | -0.008 | 2.882
6121 | 1801 | 3.3987 | 0 | 0 | 0 | 28.2543 | 8.6115 | 3.2715 | 22.0363 | 1.2234 | -0.0039329 | -0.0039047 | -0.008 | -0.0064 | 1.8359
6131 | 1811 | 3.3854 | 0 | 0 | 0 | 28.2333 | 8.6051 | 3.2651 | 22.0354 | 1.2195 | -0.0039047 | -0.0038769 | -0.0064 | -0.014 | 2.6286
6141 | 1821 | 3.3723 | 0 | 0 | 0 | 28.1874 | 8.5911 | 3.2511 | 22.0274 | 1.2156 | -0.0038769 | -0.0038494 | -0.014 | -0.0074 | 2.7638
6151 | 1831 | 3.3594 | 0 | 0 | 0 | 28.1631 | 8.5837 | 3.2437 | 22.0271 | 1.2118 | -0.0038494 | -0.0038222 | -0.0074 | -0.0117 | 2.4937
6161 | 1841 | 3.3466 | 0 | 0 | 0 | 28.1247 | 8.572 | 3.232 | 22.0189 | 1.2079 | -0.0038222 | -0.0037953 | -0.0117 | -0.0117 | 3.0719
6171 | 1851 | 3.3339 | 0 | 0 | 0 | 28.0863 | 8.5603 | 3.2203 | 22.014 | 1.2041 | -0.0037953 | -0.0037688 | -0.0117 | -0.0083 | 2.641 | -0.029431 | -0.027877 | -0.0857 | -0.0892 | 3.0597
6181 | 1861 | 3.3213 | 0 | 0 | 0 | 28.0591 | 8.552 | 3.212 | 22.0066 | 1.2004 | -0.0037688 | -0.0037425 | -0.0083 | -0.0126 | 2.7865
6191 | 1871 | 3.3089 | 0 | 0 | 0 | 28.0178 | 8.5394 | 3.1994 | 22.0058 | 1.1966 | -0.0037425 | -0.0037166 | -0.0126 | -0.0105 | 3.095
6201 | 1881 | 3.2967 | 0 | 0 | 0 | 27.9833 | 8.5289 | 3.1889 | 22.0064 | 1.1929 | -0.0037166 | -0.0036909 | -0.0105 | -0.0096 | 2.7127
6211 | 1891 | 3.2845 | 0 | 0 | 0 | 27.9518 | 8.5193 | 3.1793 | 21.994 | 1.1892 | -0.0036909 | -0.0036655 | -0.0096 | -0.0118 | 2.9112
6221 | 1901 | 3.2725 | 0 | 0 | 0 | 27.9131 | 8.5075 | 3.1675 | 21.986 | 1.1856 | -0.0036655 | -0.0036404 | -0.0118 | -0.0118 | 3.2303
6231 | 1911 | 3.2606 | 0 | 0 | 0 | 27.8744 | 8.4957 | 3.1557 | 22.0085 | 1.1819 | -0.0036404 | -0.0036156 | -0.0118 | -0.0085 | 2.7946
6241 | 1921 | 3.2488 | 0 | 0 | 0 | 27.8465 | 8.4872 | 3.1472 | 21.9945 | 1.1783 | -0.0036156 | -0.0035911 | -0.0085 | -0.0126 | 2.9318
6251 | 1931 | 3.2372 | 0 | 0 | 0 | 27.8052 | 8.4746 | 3.1346 | 21.9939 | 1.1747 | -0.0035911 | -0.0035668 | -0.0126 | -0.0138 | 3.6894 | -0.027877 | -0.026453 | -0.0892 | -0.0901 | 3.3056
6261 | 1941 | 3.2257 | 0 | 0 | 0 | 27.7599 | 8.4608 | 3.1208 | 21.9843 | 1.1711 | -0.0035668 | -0.0035428 | -0.0138 | -0.0076 | 3.0042
6271 | 1951 | 3.2142 | 0 | 0 | 0 | 27.7349 | 8.4532 | 3.1132 | 21.9861 | 1.1676 | -0.0035428 | -0.0035191 | -0.0076 | -0.0128 | 2.8937
6281 | 1961 | 3.203 | 0 | 0 | 0 | 27.693 | 8.4404 | 3.1004 | 21.9696 | 1.1641 | -0.0035191 | -0.0034956 | -0.0128 | -0.0143 | 3.8648
6291 | 1971 | 3.1918 | 0 | 0 | 0 | 27.646 | 8.4261 | 3.0861 | 21.962 | 1.1606 | -0.0034956 | -0.0034724 | -0.0143 | -0.0089 | 3.3244
6301 | 1981 | 3.1807 | 0 | 0 | 0 | 27.6168 | 8.4172 | 3.0772 | 21.9624 | 1.1571 | -0.0034724 | -0.0034495 | -0.0089 | -0.0091 | 2.6007
6311 | 1991 | 3.1698 | 0 | 0 | 0 | 27.587 | 8.4081 | 3.0681 | 21.9629 | 1.1537 | -0.0034495 | -0.0034267 | -0.0091 | -0.0154 | 3.5691
6321 | 2001 | 3.1589 | 0 | 0 | 0 | 27.5364 | 8.3927 | 3.0527 | 21.952 | 1.1502 | -0.0034267 | -0.0034043 | -0.0154 | -0.0073 | 3.3153
6331 | 2011 | 3.1482 | 0 | 0 | 0 | 27.5125 | 8.3854 | 3.0454 | 21.9477 | 1.1468 | -0.0034043 | -0.003382 | -0.0073 | -0.0145 | 3.2194 | -0.026453 | -0.025144 | -0.0901 | -0.0735 | 3.1585
6341 | 2021 | 3.1376 | 0 | 0 | 0 | 27.4649 | 8.3709 | 3.0309 | 21.936 | 1.1434 | -0.003382 | -0.00336 | -0.0145 | -0.0098 | 3.5998
6351 | 2031 | 3.127 | 0 | 0 | 0 | 27.4328 | 8.3611 | 3.0211 | 21.9191 | 1.1401 | -0.00336 | -0.0033383 | -0.0098 | -0.0076 | 2.5956
6361 | 2041 | 3.1166 | 0 | 0 | 0 | 27.4078 | 8.3535 | 3.0135 | 21.9254 | 1.1367 | -0.0033383 | -0.0033167 | -0.0076 | -0.0177 | 3.8115
6371 | 2051 | 3.1063 | 0 | 0 | 0 | 27.3498 | 8.3358 | 2.9958 | 21.9051 | 1.1334 | -0.0033167 | -0.0032954 | -0.0177 | -0.0097 | 4.1361
6381 | 2061 | 3.0961 | 0 | 0 | 0 | 27.3179 | 8.3261 | 2.9861 | 21.9028 | 1.1301 | -0.0032954 | -0.0032744 | -0.0097 | -0.0092 | 2.8764
6391 | 2071 | 3.0859 | 0 | 0 | 0 | 27.2877 | 8.3169 | 2.9769 | 21.9109 | 1.1269 | -0.0032744 | -0.0032535 | -0.0092 | -0.0117 | 3.2042
6401 | 2081 | 3.0759 | 0 | 0 | 0 | 27.2494 | 8.3052 | 2.9652 | 21.9085 | 1.1236 | -0.0032535 | -0.0032328 | -0.0117 | -0.0099 | 3.3284
6411 | 2091 | 3.066 | 0 | 0 | 0 | 27.2169 | 8.2953 | 2.9553 | 21.9224 | 1.1204 | -0.0032328 | -0.0032124 | -0.0099 | -0.0099 | 3.0721 | -0.025144 | -0.023937 | -0.0735 | -0.0665 | 2.8488
6421 | 2101 | 3.0562 | 0 | 0 | 0 | 27.1844 | 8.2854 | 2.9454 | 21.9119 | 1.1172 | -0.0032124 | -0.0031922 | -0.0099 | -0.0096 | 3.0445
6431 | 2111 | 3.0464 | 0 | 0 | 0 | 27.1529 | 8.2758 | 2.9358 | 21.9111 | 1.114 | -0.0031922 | -0.0031721 | -0.0096 | -0.0084 | 2.8271
6441 | 2121 | 3.0368 | 0 | 0 | 0 | 27.1253 | 8.2674 | 2.9274 | 21.9219 | 1.1108 | -0.0031721 | -0.0031523 | -0.0084 | -0.0123 | 3.2769
6451 | 2131 | 3.0272 | 0 | 0 | 0 | 27.085 | 8.2551 | 2.9151 | 21.9077 | 1.1076 | -0.0031523 | -0.0031327 | -0.0123 | -0.0083 | 3.2737
6461 | 2141 | 3.0177 | 0 | 0 | 0 | 27.0578 | 8.2468 | 2.9068 | 21.9118 | 1.1045 | -0.0031327 | -0.0031133 | -0.0083 | -0.0088 | 2.7383
6471 | 2151 | 3.0084 | 0 | 0 | 0 | 27.0289 | 8.238 | 2.898 | 21.902 | 1.1014 | -0.0031133 | -0.0030941 | -0.0088 | -0.008 | 2.7057
6481 | 2161 | 2.9991 | 0 | 0 | 0 | 27.0026 | 8.23 | 2.89 | 21.8964 | 1.0983 | -0.0030941 | -0.003075 | -0.008 | -0.0082 | 2.6262
6491 | 2171 | 2.9899 | 0 | 0 | 0 | 26.9757 | 8.2218 | 2.8818 | 21.8835 | 1.0952 | -0.003075 | -0.0030562 | -0.0082 | -0.0117 | 3.2493 | -0.023937 | -0.022822 | -0.0665 | -0.0407 | 2.2689
6501 | 2181 | 2.9807 | 0 | 0 | 0 | 26.9373 | 8.2101 | 2.8701 | 21.8755 | 1.0922 | -0.0030562 | -0.0030375 | -0.0117 | -0.0085 | 3.3117
6511 | 2191 | 2.9717 | 0 | 0 | 0 | 26.9094 | 8.2016 | 2.8616 | 21.8663 | 1.0891 | -0.0030375 | -0.0030191 | -0.0085 | -0.0081 | 2.7405
6521 | 2201 | 2.9627 | 0 | 0 | 0 | 26.8829 | 8.1935 | 2.8535 | 21.8589 | 1.0861 | -0.0030191 | -0.0030008 | -0.0081 | -0.0065 | 2.4237
6531 | 2211 | 2.9539 | 0 | 0 | 0 | 26.8615 | 8.187 | 2.847 | 21.8626 | 1.0831 | -0.0030008 | -0.0029827 | -0.0065 | -0.0077 | 2.3745
6541 | 2221 | 2.9451 | 0 | 0 | 0 | 26.8363 | 8.1793 | 2.8393 | 21.8648 | 1.0801 | -0.0029827 | -0.0029647 | -0.0077 | -0.0064 | 2.3695
6551 | 2231 | 2.9364 | 0 | 0 | 0 | 26.8153 | 8.1729 | 2.8329 | 21.8738 | 1.0772 | -0.0029647 | -0.002947 | -0.0064 | -0.0047 | 1.8759
6561 | 2241 | 2.9277 | 0 | 0 | 0 | 26.7999 | 8.1682 | 2.8282 | 21.8823 | 1.0742 | -0.002947 | -0.0029294 | -0.0047 | -0.0129 | 3.0035
6571 | 2251 | 2.9191 | 0 | 0 | 0 | 26.7575 | 8.1553 | 2.8153 | 21.8855 | 1.0713 | -0.0029294 | -0.0029119 | -0.0129 | -0.0017 | 2.488 | -0.022822 | -0.021788 | -0.0407 | -0.052 | 2.092
6581 | 2261 | 2.9107 | 0 | 0 | 0 | 26.752 | 8.1536 | 2.8136 | 21.8935 | 1.0684 | -0.0029119 | -0.0028947 | -0.0017 | -0.0074 | 1.573
6591 | 2271 | 2.9022 | 0 | 0 | 0 | 26.7277 | 8.1462 | 2.8062 | 21.9042 | 1.0655 | -0.0028947 | -0.0028776 | -0.0074 | -0.0047 | 2.0935
6601 | 2281 | 2.8939 | 0 | 0 | 0 | 26.7123 | 8.1415 | 2.8015 | 21.9115 | 1.0626 | -0.0028776 | -0.0028607 | -0.0047 | -0.0074 | 2.1115
6611 | 2291 | 2.8856 | 0 | 0 | 0 | 26.688 | 8.1341 | 2.7941 | 21.9124 | 1.0597 | -0.0028607 | -0.0028439 | -0.0074 | -0.003 | 1.8186
6621 | 2301 | 2.8774 | 0 | 0 | 0 | 26.6781 | 8.1311 | 2.7911 | 22.0513 | 1.0569 | -0.0028439 | -0.0028273 | -0.003 | -0.0062 | 1.6256
6631 | 2311 | 2.8693 | 0 | 0 | 0 | 26.6578 | 8.1249 | 2.7849 | 22.1512 | 1.0541 | -0.0028273 | -0.0028109 | -0.0062 | -0.0097 | 2.8237
6641 | 2321 | 2.8613 | 0 | 0 | 0 | 26.626 | 8.1152 | 2.7752 | 22.2051 | 1.0513 | -0.0028109 | -0.0027946 | -0.0097 | -0.0006 | 1.8281
6651 | 2331 | 2.8533 | 0 | 0 | 0 | 26.624 | 8.1146 | 2.7746 | 22.2455 | 1.0485 | -0.0027946 | -0.0027784 | -0.0006 | -0.0093 | 1.7855 | -0.021788 | -0.020827 | -0.052 | -0.0461 | 2.2981
6661 | 2341 | 2.8454 | 0 | 0 | 0 | 26.5935 | 8.1053 | 2.7653 | 22.2695 | 1.0457 | -0.0027784 | -0.0027624 | -0.0093 | -0.0033 | 2.2678
6671 | 2351 | 2.8375 | 0 | 0 | 0 | 26.5827 | 8.102 | 2.762 | 22.3015 | 1.0429 | -0.0027624 | -0.0027466 | -0.0033 | -0.0087 | 2.1839
6681 | 2361 | 2.8297 | 0 | 0 | 0 | 26.5541 | 8.0933 | 2.7533 | 22.3113 | 1.0402 | -0.0027466 | -0.0027309 | -0.0087 | -0.0047 | 2.4422
6691 | 2371 | 2.822 | 0 | 0 | 0 | 26.5387 | 8.0886 | 2.7486 | 22.3275 | 1.0375 | -0.0027309 | -0.0027153 | -0.0047 | -0.0077 | 2.28
6701 | 2381 | 2.8144 | 0 | 0 | 0 | 26.5134 | 8.0809 | 2.7409 | 22.3383 | 1.0347 | -0.0027153 | -0.0026999 | -0.0077 | -0.0032 | 2.0081
6711 | 2391 | 2.8068 | 0 | 0 | 0 | 26.5029 | 8.0777 | 2.7377 | 22.3435 | 1.032 | -0.0026999 | -0.0026846 | -0.0032 | -0.0052 | 1.5621
6721 | 2401 | 2.7993 | 0 | 0 | 0 | 26.4859 | 8.0725 | 2.7325 | 22.3357 | 1.0294 | -0.0026846 | -0.0026695 | -0.0052 | -0.0099 | 2.8252
6731 | 2411 | 2.7918 | 0 | 0 | 0 | 26.4534 | 8.0626 | 2.7226 | 22.3333 | 1.0267 | -0.0026695 | -0.0026545 | -0.0099 | -0.0021 | 2.2457 | -0.020827 | -0.019933 | -0.0461 | -0.0632 | 2.7025
6741 | 2421 | 2.7844 | 0 | 0 | 0 | 26.4465 | 8.0605 | 2.7205 | 22.334 | 1.024 | -0.0026545 | -0.0026397 | -0.0021 | -0.0065 | 1.6291
6751 | 2431 | 2.777 | 0 | 0 | 0 | 26.4252 | 8.054 | 2.714 | 22.3547 | 1.0214 | -0.0026397 | -0.0026249 | -0.0065 | -0.0056 | 2.2975
6761 | 2441 | 2.7698 | 0 | 0 | 0 | 26.4068 | 8.0484 | 2.7084 | 22.3628 | 1.0188 | -0.0026249 | -0.0026103 | -0.0056 | -0.0067 | 2.3507
6771 | 2451 | 2.7625 | 0 | 0 | 0 | 26.3848 | 8.0417 | 2.7017 | 22.3761 | 1.0162 | -0.0026103 | -0.0025959 | -0.0067 | -0.0055 | 2.3421
6781 | 2461 | 2.7554 | 0 | 0 | 0 | 26.3668 | 8.0362 | 2.6962 | 22.3798 | 1.0136 | -0.0025959 | -0.0025815 | -0.0055 | -0.0077 | 2.5519
6791 | 2471 | 2.7483 | 0 | 0 | 0 | 26.3415 | 8.0285 | 2.6885 | 22.3811 | 1.011 | -0.0025815 | -0.0025673 | -0.0077 | -0.0037 | 2.2098
6801 | 2481 | 2.7412 | 0 | 0 | 0 | 26.3294 | 8.0248 | 2.6848 | 22.3826 | 1.0084 | -0.0025673 | -0.0025532 | -0.0037 | -0.0083 | 2.3485
6811 | 2491 | 2.7342 | 0 | 0 | 0 | 26.3021 | 8.0165 | 2.6765 | 22.3884 | 1.0059 | -0.0025532 | -0.0025393 | -0.0083 | -0.0079 | 3.1808 | -0.019933 | -0.0191 | -0.0632 | -0.0664 | 3.3268
6821 | 2501 | 2.7273 | 0 | 0 | 0 | 26.2762 | 8.0086 | 2.6686 | 22.3852 | 1.0033 | -0.0025393 | -0.0025254 | -0.0079 | -0.0067 | 2.8814
6831 | 2511 | 2.7204 | 0 | 0 | 0 | 26.2542 | 8.0019 | 2.6619 | 22.3909 | 1.0008 | -0.0025254 | -0.0025117 | -0.0067 | -0.0115 | 3.6184
6841 | 2521 | 2.7136 | 0 | 0 | 0 | 26.2165 | 7.9904 | 2.6504 | 22.391 | 0.99828 | -0.0025117 | -0.0024981 | -0.0115 | -0.0047 | 3.2263
6851 | 2531 | 2.7068 | 0 | 0 | 0 | 26.2011 | 7.9857 | 2.6457 | 22.3966 | 0.99578 | -0.0024981 | -0.0024846 | -0.0047 | -0.0079 | 2.5322
6861 | 2541 | 2.7001 | 0 | 0 | 0 | 26.1752 | 7.9778 | 2.6378 | 22.3884 | 0.9933 | -0.0024846 | -0.0024713 | -0.0079 | -0.0072 | 3.0461
6871 | 2551 | 2.6935 | 0 | 0 | 0 | 26.1515 | 7.9706 | 2.6306 | 22.3932 | 0.99082 | -0.0024713 | -0.002458 | -0.0072 | -0.0073 | 2.9417
6881 | 2561 | 2.6868 | 0 | 0 | 0 | 26.1276 | 7.9633 | 2.6233 | 22.3955 | 0.98837 | -0.002458 | -0.0024449 | -0.0073 | -0.01 | 3.5315
6891 | 2571 | 2.6803 | 0 | 0 | 0 | 26.0948 | 7.9533 | 2.6133 | 22.3972 | 0.98592 | -0.0024449 | -0.0024319 | -0.01 | -0.0055 | 3.1734 | -0.0191 | -0.01832 | -0.0664 | -0.0668 | 3.5632
6901 | 2581 | 2.6738 | 0 | 0 | 0 | 26.0767 | 7.9478 | 2.6078 | 22.396 | 0.98349 | -0.0024319 | -0.002419 | -0.0055 | -0.0068 | 2.5371
6911 | 2591 | 2.6673 | 0 | 0 | 0 | 26.0544 | 7.941 | 2.601 | 22.3941 | 0.98107 | -0.002419 | -0.0024062 | -0.0068 | -0.0148 | 4.4854
6921 | 2601 | 2.6609 | 0 | 0 | 0 | 26.0059 | 7.9262 | 2.5862 | 22.3838 | 0.97866 | -0.0024062 | -0.0023935 | -0.0148 | -0.0051 | 4.1355
6931 | 2611 | 2.6545 | 0 | 0 | 0 | 25.9891 | 7.9211 | 2.5811 | 22.384 | 0.97627 | -0.0023935 | -0.0023809 | -0.0051 | -0.007 | 2.5365
6941 | 2621 | 2.6482 | 0 | 0 | 0 | 25.9662 | 7.9141 | 2.5741 | 22.3739 | 0.97389 | -0.0023809 | -0.0023684 | -0.007 | -0.0086 | 3.2865
6951 | 2631 | 2.642 | 0 | 0 | 0 | 25.9379 | 7.9055 | 2.5655 | 22.3693 | 0.97152 | -0.0023684 | -0.002356 | -0.0086 | -0.0076 | 3.4279
6961 | 2641 | 2.6357 | 0 | 0 | 0 | 25.913 | 7.8979 | 2.5579 | 22.3767 | 0.96917 | -0.002356 | -0.0023437 | -0.0076 | -0.011 | 3.9615
6971 | 2651 | 2.6296 | 0 | 0 | 0 | 25.8769 | 7.8869 | 2.5469 | 22.3556 | 0.96682 | -0.0023437 | -0.0023316 | -0.011 | -0.0067 | 3.7811 | -0.01832 | -0.01759 | -0.0668 | -0.0587 | 3.4885
6981 | 2661 | 2.6234 | 0 | 0 | 0 | 25.8549 | 7.8802 | 2.5402 | 22.3564 | 0.96449 | -0.0023316 | -0.0023195 | -0.0067 | -0.0082 | 3.2053
6991 | 2671 | 2.6174 | 0 | 0 | 0 | 25.828 | 7.872 | 2.532 | 22.3523 | 0.96217 | -0.0023195 | -0.0023075 | -0.0082 | -0.0031 | 2.4365
7001 | 2681 | 2.6113 | 0 | 0 | 0 | 25.8179 | 7.8689 | 2.5289 | 22.3587 | 0.95986 | -0.0023075 | -0.0022957 | -0.0031 | -0.0146 | 3.8581
7011 | 2691 | 2.6054 | 0 | 0 | 0 | 25.77 | 7.8543 | 2.5143 | 22.3499 | 0.95757 | -0.0022957 | -0.0022839 | -0.0146 | -0.0103 | 5.4325
7021 | 2701 | 2.5994 | 0 | 0 | 0 | 25.7362 | 7.844 | 2.504 | 22.3405 | 0.95528 | -0.0022839 | -0.0022722 | -0.0103 | -0.0066 | 3.7052
7031 | 2711 | 2.5935 | 0 | 0 | 0 | 25.7145 | 7.8374 | 2.4974 | 22.3464 | 0.95301 | -0.0022722 | -0.0022606 | -0.0066 | -0.0093 | 3.5108
7041 | 2721 | 2.5877 | 0 | 0 | 0 | 25.684 | 7.8281 | 2.4881 | 22.3368 | 0.95075 | -0.0022606 | -0.0022491 | -0.0093 | -0.008 | 3.8347
7051 | 2731 | 2.5818 | 0 | 0 | 0 | 25.6577 | 7.8201 | 2.4801 | 22.3349 | 0.9485 | -0.0022491 | -0.0022377 | -0.008 | -0.0043 | 2.7372 | -0.01759 | -0.016906 | -0.0587 | -0.0466 | 3.041
7061 | 2741 | 2.5761 | 0 | 0 | 0 | 25.6436 | 7.8158 | 2.4758 | 22.3306 | 0.94626 | -0.0022377 | -0.0022264 | -0.0043 | -0.0127 | 3.8177
7071 | 2751 | 2.5703 | 0 | 0 | 0 | 25.602 | 7.8031 | 2.4631 | 22.3358 | 0.94404 | -0.0022264 | -0.0022152 | -0.0127 | -0.0043 | 3.8179
7081 | 2761 | 2.5647 | 0 | 0 | 0 | 25.5879 | 7.7988 | 2.4588 | 22.3332 | 0.94182 | -0.0022152 | -0.0022041 | -0.0043 | -0.009 | 3.0149
7091 | 2771 | 2.559 | 0 | 0 | 0 | 25.5583 | 7.7898 | 2.4498 | 22.3265 | 0.93962 | -0.0022041 | -0.0021931 | -0.009 | -0.0101 | 4.345
7101 | 2781 | 2.5534 | 0 | 0 | 0 | 25.5252 | 7.7797 | 2.4397 | 22.3256 | 0.93743 | -0.0021931 | -0.0021821 | -0.0101 | -0.0066 | 3.813
7111 | 2791 | 2.5478 | 0 | 0 | 0 | 25.5035 | 7.7731 | 2.4331 | 22.3248 | 0.93524 | -0.0021821 | -0.0021713 | -0.0066 | -0.0016 | 1.8779
7121 | 2801 | 2.5423 | 0 | 0 | 0 | 25.4983 | 7.7715 | 2.4315 | 22.3257 | 0.93307 | -0.0021713 | -0.0021605 | -0.0016 | -0.0101 | 2.7108
7131 | 2811 | 2.5368 | 0 | 0 | 0 | 25.4652 | 7.7614 | 2.4214 | 22.3224 | 0.93091 | -0.0021605 | -0.0021498 | -0.0101 | -0.0082 | 4.2435 | -0.016906 | -0.016263 | -0.0466 | -0.0257 | 2.1569
7141 | 2821 | 2.5314 | 0 | 0 | 0 | 25.4382 | 7.7532 | 2.4132 | 22.3162 | 0.92876 | -0.0021498 | -0.0021392 | -0.0082 | -0.0046 | 2.9803
7151 | 2831 | 2.526 | 0 | 0 | 0 | 25.4232 | 7.7486 | 2.4086 | 22.3142 | 0.92662 | -0.0021392 | -0.0021287 | -0.0046 | -0.0048 | 2.2028
7161 | 2841 | 2.5206 | 0 | 0 | 0 | 25.4074 | 7.7438 | 2.4038 | 22.3172 | 0.92449 | -0.0021287 | -0.0021182 | -0.0048 | -0.0064 | 2.6391
7171 | 2851 | 2.5153 | 0 | 0 | 0 | 25.3864 | 7.7374 | 2.3974 | 22.3157 | 0.92238 | -0.0021182 | -0.0021079 | -0.0064 | -0.0055 | 2.8148
7181 | 2861 | 2.51 | 0 | 0 | 0 | 25.3684 | 7.7319 | 2.3919 | 22.3109 | 0.92027 | -0.0021079 | -0.0020976 | -0.0055 | -0.008 | 3.2131
7191 | 2871 | 2.5047 | 0 | 0 | 0 | 25.3421 | 7.7239 | 2.3839 | 22.307 | 0.91817 | -0.0020976 | -0.0020874 | -0.008 | -0.0018 | 2.3345
7201 | 2881 | 2.4995 | 0 | 0 | 0 | 25.3362 | 7.7221 | 2.3821 | 22.3048 | 0.91608 | -0.0020874 | -0.0020773 | -0.0018 | -0.0073 | 2.1915
7211 | 2891 | 2.4943 | 0 | 0 | 0 | 25.3123 | 7.7148 | 2.3748 | 22.2975 | 0.91401 | -0.0020773 | -0.0020672 | -0.0073 | -0.0025 | 2.359 | -0.016263 | -0.015658 | -0.0257 | -0.0155 | 1.2795
7221 | 2901 | 2.4891 | 0 | 0 | 0 | 25.3041 | 7.7123 | 2.3723 | 22.3009 | 0.91194 | -0.0020672 | -0.0020573 | -0.0025 | -0.0112 | 3.3318
7231 | 2911 | 2.484 | 0 | 0 | 0 | 25.2673 | 7.7011 | 2.3611 | 22.2897 | 0.90988 | -0.0020573 | -0.0020474 | -0.0112 | -0.0023 | 3.2785
7241 | 2921 | 2.4789 | 0 | 0 | 0 | 25.2598 | 7.6988 | 2.3588 | 22.3033 | 0.90783 | -0.0020474 | -0.0020376 | -0.0023 | 0.0008 | 0.36356
7251 | 2931 | 2.4739 | 0 | 0 | 0 | 25.2624 | 7.6996 | 2.3596 | 22.3247 | 0.9058 | -0.0020376 | -0.0020278 | 0.0008 | -0.0033 | 0.61979
7261 | 2941 | 2.4689 | 0 | 0 | 0 | 25.2516 | 7.6963 | 2.3563 | 22.3292 | 0.90377 | -0.0020278 | -0.0020182 | -0.0033 | -0.0012 | 1.1097
7271 | 2951 | 2.4639 | 0 | 0 | 0 | 25.2476 | 7.6951 | 2.3551 | 21.9265 | 0.90175 | -0.0020182 | -0.0020086 | -0.0012 | -0.0025 | 0.92041
7281 | 2961 | 2.459 | 0 | 0 | 0 | 25.2394 | 7.6926 | 2.3526 | 21.9782 | 0.89974 | -0.0020086 | -0.0019991 | -0.0025 | -0.0035 | 1.4983
7291 | 2971 | 2.4541 | 0 | 0 | 0 | 25.2279 | 7.6891 | 2.3491 | 22.0092 | 0.89774 | -0.0019991 | -0.0019896 | -0.0035 | 0.0006 | 0.7222 | -0.015658 | -0.015088 | -0.0155 | -0.0295 | 1.4815
7301 | 2981 | 2.4492 | 0 | 0 | 0 | 25.2299 | 7.6897 | 2.3497 | 22.0325 | 0.89575 | -0.0019896 | -0.0019802 | 0.0006 | -0.004 | 0.86194
7311 | 2991 | 2.4443 | 0 | 0 | 0 | 25.2168 | 7.6857 | 2.3457 | 22.0375 | 0.89377 | -0.0019802 | -0.0019709 | -0.004 | 0.0006 | 0.85503
7321 | 3001 | 2.4395 | 0 | 0 | 0 | 25.2188 | 7.6863 | 2.3463 | 22.0417 | 0.8918 | -0.0019709 | -0.0019617 | 0.0006 | 0.0018 | -0.61172
7331 | 3011 | 2.4347 | 0 | 0 | 0 | 25.2247 | 7.6881 | 2.3481 | 22.0346 | 0.88984 | -0.0019617 | -0.0019525 | 0.0018 | -0.0055 | 0.95403
7341 | 3021 | 2.43 | 0 | 0 | 0 | 25.2066 | 7.6826 | 2.3426 | 22.0433 | 0.88789 | -0.0019525 | -0.0019434 | -0.0055 | -0.0036 | 2.3335
7351 | 3031 | 2.4253 | 0 | 0 | 0 | 25.1948 | 7.679 | 2.339 | 22.0347 | 0.88594 | -0.0019434 | -0.0019344 | -0.0036 | -0.0041 | 1.9863
7361 | 3041 | 2.4206 | 0 | 0 | 0 | 25.1813 | 7.6749 | 2.3349 | 22.0287 | 0.88401 | -0.0019344 | -0.0019254 | -0.0041 | -0.0013 | 1.3957
7371 | 3051 | 2.4159 | 0 | 0 | 0 | 25.1771 | 7.6736 | 2.3336 | 22.0377 | 0.88208 | -0.0019254 | -0.0019165 | -0.0013 | -0.001 | 0.5983 | -0.015088 | -0.01455 | -0.0295 | -0.0348 | 2.1774
7381 | 3061 | 2.4113 | 0 | 0 | 0 | 25.1738 | 7.6726 | 2.3326 | 22.034 | 0.88017 | -0.0019165 | -0.0019077 | -0.001 | -0.007 | 2.0992
7391 | 3071 | 2.4067 | 0 | 0 | 0 | 25.1508 | 7.6656 | 2.3256 | 22.0231 | 0.87826 | -0.0019077 | -0.0018989 | -0.007 | -0.0038 | 2.8334
7401 | 3081 | 2.4021 | 0 | 0 | 0 | 25.1384 | 7.6618 | 2.3218 | 22.0251 | 0.87636 | -0.0018989 | -0.0018902 | -0.0038 | -0.0051 | 2.3505
7411 | 3091 | 2.3976 | 0 | 0 | 0 | 25.1216 | 7.6567 | 2.3167 | 22.012 | 0.87447 | -0.0018902 | -0.0018815 | -0.0051 | -0.0029 | 2.1184
7421 | 3101 | 2.3931 | 0 | 0 | 0 | 25.1121 | 7.6538 | 2.3138 | 22.0071 | 0.87259 | -0.0018815 | -0.001873 | -0.0029 | 0.0042 | -0.3549
7431 | 3111 | 2.3886 | 0 | 0 | 0 | 25.1259 | 7.658 | 2.318 | 22.013 | 0.87072 | -0.001873 | -0.0018644 | 0.0042 | -0.0108 | 1.7843
7441 | 3121 | 2.3842 | 0 | 0 | 0 | 25.0905 | 7.6472 | 2.3072 | 22.0277 | 0.86885 | -0.0018644 | -0.001856 | -0.0108 | -0.0031 | 3.7268
7451 | 3131 | 2.3798 | 0 | 0 | 0 | 25.0803 | 7.6441 | 2.3041 | 22.0302 | 0.867 | -0.001856 | -0.0018476 | -0.0031 | 0.0029 | 0.046654 | -0.01455 | -0.014042 | -0.0348 | -0.0522 | 3.0663
7461 | 3141 | 2.3754 | 0 | 0 | 0 | 25.0898 | 7.647 | 2.307 | 22.0391 | 0.86515 | -0.0018476 | -0.0018392 | 0.0029 | -0.0054 | 0.68828
7471 | 3151 | 2.371 | 0 | 0 | 0 | 25.0721 | 7.6416 | 2.3016 | 22.0298 | 0.86331 | -0.0018392 | -0.001831 | -0.0054 | -0.0125 | 4.8859
7481 | 3161 | 2.3667 | 0 | 0 | 0 | 25.0311 | 7.6291 | 2.2891 | 22.0241 | 0.86148 | -0.001831 | -0.0018227 | -0.0125 | -0.0004 | 3.5158
7491 | 3171 | 2.3623 | 0 | 0 | 0 | 25.0298 | 7.6287 | 2.2887 | 22.0209 | 0.85966 | -0.0018227 | -0.0018146 | -0.0004 | -0.0041 | 1.2418
7501 | 3181 | 2.3581 | 0 | 0 | 0 | 25.0163 | 7.6246 | 2.2846 | 22.0179 | 0.85784 | -0.0018146 | -0.0018065 | -0.0041 | -0.0059 | 2.7639
7511 | 3191 | 2.3538 | 0 | 0 | 0 | 24.997 | 7.6187 | 2.2787 | 22.0082 | 0.85603 | -0.0018065 | -0.0017984 | -0.0059 | -0.0026 | 2.3538
7521 | 3201 | 2.3496 | 0 | 0 | 0 | 24.9884 | 7.6161 | 2.2761 | 22.0125 | 0.85424 | -0.0017984 | -0.0017904 | -0.0026 | -0.0068 | 2.6245
7531 | 3211 | 2.3454 | 0 | 0 | 0 | 24.9661 | 7.6093 | 2.2693 | 22.0065 | 0.85245 | -0.0017904 | -0.0017825 | -0.0068 | -0.0076 | 4.0314 | -0.014042 | -0.013562 | -0.0522 | -0.0616 | 4.1369
7541 | 3221 | 2.3412 | 0 | 0 | 0 | 24.9412 | 7.6017 | 2.2617 | 21.9987 | 0.85066 | -0.0017825 | -0.0017746 | -0.0076 | -0.0019 | 2.6636
7551 | 3231 | 2.337 | 0 | 0 | 0 | 24.9349 | 7.5998 | 2.2598 | 22 | 0.84889 | -0.0017746 | -0.0017668 | -0.0019 | -0.0065 | 2.3777
7561 | 3241 | 2.3329 | 0 | 0 | 0 | 24.9136 | 7.5933 | 2.2533 | 22.0008 | 0.84712 | -0.0017668 | -0.001759 | -0.0065 | -0.0091 | 4.4278
7571 | 3251 | 2.3288 | 0 | 0 | 0 | 24.8838 | 7.5842 | 2.2442 | 21.9858 | 0.84536 | -0.001759 | -0.0017513 | -0.0091 | -0.0032 | 3.4966
7581 | 3261 | 2.3247 | 0 | 0 | 0 | 24.8733 | 7.581 | 2.241 | 21.9909 | 0.84361 | -0.0017513 | -0.0017436 | -0.0032 | -0.0068 | 2.8658
7591 | 3271 | 2.3207 | 0 | 0 | 0 | 24.851 | 7.5742 | 2.2342 | 21.9802 | 0.84187 | -0.0017436 | -0.001736 | -0.0068 | -0.0093 | 4.6301
7601 | 3281 | 2.3167 | 0 | 0 | 0 | 24.8204 | 7.5649 | 2.2249 | 21.9592 | 0.84013 | -0.001736 | -0.0017285 | -0.0093 | -0.0078 | 4.934
7611 | 3291 | 2.3127 | 0 | 0 | 0 | 24.7948 | 7.5571 | 2.2171 | 21.9485 | 0.8384 | -0.0017285 | -0.001721 | -0.0078 | -0.0061 | 4.0276 | -0.013562 | -0.013107 | -0.0616 | -0.0723 | 5.0376
7621 | 3301 | 2.3087 | 0 | 0 | 0 | 24.7748 | 7.551 | 2.211 | 21.9513 | 0.83668 | -0.001721 | -0.0017135 | -0.0061 | -0.006 | 3.523
7631 | 3311 | 2.3047 | 0 | 0 | 0 | 24.7551 | 7.545 | 2.205 | 21.9446 | 0.83497 | -0.0017135 | -0.0017061 | -0.006 | -0.0102 | 4.7428
7641 | 3321 | 2.3008 | 0 | 0 | 0 | 24.7217 | 7.5348 | 2.1948 | 21.9393 | 0.83326 | -0.0017061 | -0.0016987 | -0.0102 | -0.0059 | 4.7232
7651 | 3331 | 2.2969 | 0 | 0 | 0 | 24.7023 | 7.5289 | 2.1889 | 21.9335 | 0.83156 | -0.0016987 | -0.0016914 | -0.0059 | -0.0093 | 4.4879
7661 | 3341 | 2.293 | 0 | 0 | 0 | 24.6718 | 7.5196 | 2.1796 | 21.923 | 0.82987 | -0.0016914 | -0.0016842 | -0.0093 | -0.0073 | 4.9151
7671 | 3351 | 2.2892 | 0 | 0 | 0 | 24.6479 | 7.5123 | 2.1723 | 21.9122 | 0.82819 | -0.0016842 | -0.001677 | -0.0073 | -0.0092 | 4.9115
7681 | 3361 | 2.2853 | 0 | 0 | 0 | 24.6177 | 7.5031 | 2.1631 | 21.906 | 0.82651 | -0.001677 | -0.0016698 | -0.0092 | -0.0076 | 5.0177
7691 | 3371 | 2.2815 | 0 | 0 | 0 | 24.5927 | 7.4955 | 2.1555 | 21.8963 | 0.82484 | -0.0016698 | -0.0016627 | -0.0076 | -0.0095 | 5.1337 | -0.013107 | -0.012675 | -0.0723 | -0.0703 | 5.5316
7701 | 3381 | 2.2777 | 0 | 0 | 0 | 24.5616 | 7.486 | 2.146 | 21.8784 | 0.82318 | -0.0016627 | -0.0016556 | -0.0095 | -0.0081 | 5.3021
7711 | 3391 | 2.274 | 0 | 0 | 0 | 24.535 | 7.4779 | 2.1379 | 21.8759 | 0.82152 | -0.0016556 | -0.0016486 | -0.0081 | -0.0064 | 4.3861
7721 | 3401 | 2.2702 | 0 | 0 | 0 | 24.514 | 7.4715 | 2.1315 | 21.8648 | 0.81987 | -0.0016486 | -0.0016417 | -0.0064 | -0.0094 | 4.8059
7731 | 3411 | 2.2665 | 0 | 0 | 0 | 24.4832 | 7.4621 | 2.1221 | 21.8624 | 0.81823 | -0.0016417 | -0.0016347 | -0.0094 | -0.0082 | 5.3702
7741 | 3421 | 2.2628 | 0 | 0 | 0 | 24.4562 | 7.4539 | 2.1139 | 21.8564 | 0.8166 | -0.0016347 | -0.0016279 | -0.0082 | -0.0128 | 6.4426
7751 | 3431 | 2.2591 | 0 | 0 | 0 | 24.4142 | 7.4411 | 2.1011 | 21.8438 | 0.81497 | -0.0016279 | -0.001621 | -0.0128 | -0.011 | 7.3233
7761 | 3441 | 2.2554 | 0 | 0 | 0 | 24.3782 | 7.4301 | 2.0901 | 21.83 | 0.81335 | -0.001621 | -0.0016143 | -0.011 | -0.0069 | 5.5275
7771 | 3451 | 2.2518 | 0 | 0 | 0 | 24.3555 | 7.4232 | 2.0832 | 21.8327 | 0.81173 | -0.0016143 | -0.0016075 | -0.0069 | -0.0082 | 4.6886 | -0.012675 | -0.012265 | -0.0703 | -0.0594 | 5.1888
7781 | 3461 | 2.2482 | 0 | 0 | 0 | 24.3286 | 7.415 | 2.075 | 21.8302 | 0.81013 | -0.0016075 | -0.0016008 | -0.0082 | -0.0087 | 5.2682
7791 | 3471 | 2.2446 | 0 | 0 | 0 | 24.3001 | 7.4063 | 2.0663 | 21.8237 | 0.80853 | -0.0016008 | -0.0015942 | -0.0087 | -0.0073 | 5.0061
7801 | 3481 | 2.241 | 0 | 0 | 0 | 24.2761 | 7.399 | 2.059 | 21.811 | 0.80693 | -0.0015942 | -0.0015876 | -0.0073 | -0.0094 | 5.2515
7811 | 3491 | 2.2375 | 0 | 0 | 0 | 24.2453 | 7.3896 | 2.0496 | 21.8161 | 0.80534 | -0.0015876 | -0.001581 | -0.0094 | -0.0106 | 6.3137
7821 | 3501 | 2.2339 | 0 | 0 | 0 | 24.2105 | 7.379 | 2.039 | 21.7976 | 0.80376 | -0.001581 | -0.0015745 | -0.0106 | -0.0051 | 4.9684
7831 | 3511 | 2.2304 | 0 | 0 | 0 | 24.1938 | 7.3739 | 2.0339 | 21.7962 | 0.80219 | -0.0015745 | -0.001568 | -0.0051 | -0.013 | 5.7703
7841 | 3521 | 2.2269 | 0 | 0 | 0 | 24.1511 | 7.3609 | 2.0209 | 21.7892 | 0.80062 | -0.001568 | -0.0015615 | -0.013 | -0.008 | 6.7038
7851 | 3531 | 2.2234 | 0 | 0 | 0 | 24.1249 | 7.3529 | 2.0129 | 21.7776 | 0.79906 | -0.0015615 | -0.0015551 | -0.008 | -0.0072 | 4.876 | -0.012265 | -0.011876 | -0.0594 | -0.042 | 4.1792
7861 | 3541 | 2.22 | 0 | 0 | 0 | 24.1012 | 7.3457 | 2.0057 | 21.7802 | 0.7975 | -0.0015551 | -0.0015488 | -0.0072 | -0.0093 | 5.3187
7871 | 3551 | 2.2166 | 0 | 0 | 0 | 24.0707 | 7.3364 | 1.9964 | 21.7757 | 0.79596 | -0.0015488 | -0.0015425 | -0.0093 | -0.0088 | 5.8546
7881 | 3561 | 2.2131 | 0 | 0 | 0 | 24.0419 | 7.3276 | 1.9876 | 21.7749 | 0.79441 | -0.0015425 | -0.0015362 | -0.0088 | -0.0083 | 5.5537
7891 | 3571 | 2.2097 | 0 | 0 | 0 | 24.0146 | 7.3193 | 1.9793 | 21.765 | 0.79288 | -0.0015362 | -0.00153 | -0.0083 | -0.0024 | 3.4819
7901 | 3581 | 2.2064 | 0 | 0 | 0 | 24.0067 | 7.3169 | 1.9769 | 21.7658 | 0.79135 | -0.00153 | -0.0015238 | -0.0024 | -0.0102 | 4.1365
7911 | 3591 | 2.203 | 0 | 0 | 0 | 23.9733 | 7.3067 | 1.9667 | 21.7594 | 0.78982 | -0.0015238 | -0.0015176 | -0.0102 | -0.0085 | 6.1463
7921 | 3601 | 2.1997 | 0 | 0 | 0 | 23.9454 | 7.2982 | 1.9582 | 21.7507 | 0.78831 | -0.0015176 | -0.0015115 | -0.0085 | -0.0047 | 4.3527
7931 | 3611 | 2.1963 | 0 | 0 | 0 | 23.93 | 7.2935 | 1.9535 | 21.7555 | 0.78679 | -0.0015115 | -0.0015054 | -0.0047 | -0.0096 | 4.7466 | -0.011876 | -0.011506 | -0.042 | -0.0304 | 3.0822
7941 | 3621 | 2.193 | 0 | 0 | 0 | 23.8985 | 7.2839 | 1.9439 | 21.7459 | 0.78529 | -0.0015054 | -0.0014994 | -0.0096 | -0.0027 | 4.0843
7951 | 3631 | 2.1898 | 0 | 0 | 0 | 23.8896 | 7.2812 | 1.9412 | 21.7551 | 0.78379 | -0.0014994 | -0.0014934 | -0.0027 | -0.007 | 3.247
7961 | 3641 | 2.1865 | 0 | 0 | 0 | 23.8667 | 7.2742 | 1.9342 | 21.7597 | 0.7823 | -0.0014934 | -0.0014874 | -0.007 | -0.0037 | 3.5853
7971 | 3651 | 2.1832 | 0 | 0 | 0 | 23.8545 | 7.2705 | 1.9305 | 21.7686 | 0.78081 | -0.0014874 | -0.0014815 | -0.0037 | -0.0068 | 3.5409
7981 | 3661 | 2.18 | 0 | 0 | 0 | 23.8322 | 7.2637 | 1.9237 | 21.7603 | 0.77933 | -0.0014815 | -0.0014756 | -0.0068 | -0.0014 | 2.7658
7991 | 3671 | 2.1768 | 0 | 0 | 0 | 23.8276 | 7.2623 | 1.9223 | 21.7706 | 0.77785 | -0.0014756 | -0.0014697 | -0.0014 | -0.0044 | 1.9733
8001 | 3681 | 2.1736 | 0 | 0 | 0 | 23.8132 | 7.2579 | 1.9179 | 21.7711 | 0.77638 | -0.0014697 | -0.0014639 | -0.0044 | -0.0064 | 3.6842
8011 | 3691 | 2.1704 | 0 | 0 | 0 | 23.7922 | 7.2515 | 1.9115 | 21.7662 | 0.77492 | -0.0014639 | -0.0014581 | -0.0064 | -0.0061 | 4.2775 | -0.011506 | -0.011154 | -0.0304 | -0.0274 | 2.5479
8021 | 3701 | 2.1673 | 0 | 0 | 0 | 23.7722 | 7.2454 | 1.9054 | 21.7732 | 0.77346 | -0.0014581 | -0.0014524 | -0.0061 | -0.0029 | 3.0879
8031 | 3711 | 2.1641 | 0 | 0 | 0 | 23.7626 | 7.2425 | 1.9025 | 21.7704 | 0.77201 | -0.0014524 | -0.0014467 | -0.0029 | -0.0045 | 2.5548
8041 | 3721 | 2.161 | 0 | 0 | 0 | 23.7479 | 7.238 | 1.898 | 21.7747 | 0.77056 | -0.0014467 | -0.001441 | -0.0045 | -0.0072 | 4.0554
8051 | 3731 | 2.1579 | 0 | 0 | 0 | 23.7243 | 7.2308 | 1.8908 | 21.7601 | 0.76912 | -0.001441 | -0.0014354 | -0.0072 | -0.0017 | 3.0867
8061 | 3741 | 2.1548 | 0 | 0 | 0 | 23.7187 | 7.2291 | 1.8891 | 21.7581 | 0.76768 | -0.0014354 | -0.0014297 | -0.0017 | -0.0038 | 1.9225
8071 | 3751 | 2.1517 | 0 | 0 | 0 | 23.7062 | 7.2253 | 1.8853 | 21.7552 | 0.76625 | -0.0014297 | -0.0014242 | -0.0038 | -0.002 | 2.0298
8081 | 3761 | 2.1486 | 0 | 0 | 0 | 23.6996 | 7.2233 | 1.8833 | 21.7625 | 0.76483 | -0.0014242 | -0.0014186 | -0.002 | -0.0022 | 1.4777
8091 | 3771 | 2.1456 | 0 | 0 | 0 | 23.6924 | 7.2211 | 1.8811 | 21.7709 | 0.76341 | -0.0014186 | -0.0014131 | -0.0022 | -0.0037 | 2.0856 | -0.011154 | -0.010818 | -0.0274 | -0.0234 | 2.3076
8101 | 3781 | 2.1426 | 0 | 0 | 0 | 23.6803 | 7.2174 | 1.8774 | 21.7778 | 0.762 | -0.0014131 | -0.0014077 | -0.0037 | 0.0001 | 1.271
8111 | 3791 | 2.1395 | 0 | 0 | 0 | 23.6806 | 7.2175 | 1.8775 | 21.7864 | 0.76059 | -0.0014077 | -0.0014022 | 0.0001 | -0.0037 | 1.2864
8121 | 3801 | 2.1365 | 0 | 0 | 0 | 23.6685 | 7.2138 | 1.8738 | 21.7951 | 0.75919 | -0.0014022 | -0.0013968 | -0.0037 | -0.0089 | 4.5088
8131 | 3811 | 2.1336 | 0 | 0 | 0 | 23.6393 | 7.2049 | 1.8649 | 21.794 | 0.75779 | -0.0013968 | -0.0013914 | -0.0089 | -0.0003 | 3.2877
8141 | 3821 | 2.1306 | 0 | 0 | 0 | 23.6383 | 7.2046 | 1.8646 | 21.803 | 0.7564 | -0.0013914 | -0.0013861 | -0.0003 | 0.0003 | -0.00083069
8151 | 3831 | 2.1276 | 0 | 0 | 0 | 23.6393 | 7.2049 | 1.8649 | 21.8151 | 0.75501 | -0.0013861 | -0.0013808 | 0.0003 | -0.0056 | 1.9237
8161 | 3841 | 2.1247 | 0 | 0 | 0 | 23.6209 | 7.1993 | 1.8593 | 21.8122 | 0.75363 | -0.0013808 | -0.0013755 | -0.0056 | -0.0056 | 4.0634
8171 | 3851 | 2.1218 | 0 | 0 | 0 | 23.6025 | 7.1937 | 1.8537 | 21.8016 | 0.75226 | -0.0013755 | -0.0013703 | -0.0056 | -0.0026 | 2.9822 | -0.010818 | -0.010498 | -0.0234 | -0.0348 | 2.7477
8181 | 3861 | 2.1189 | 0 | 0 | 0 | 23.594 | 7.1911 | 1.8511 | 21.8058 | 0.75089 | -0.0013703 | -0.0013651 | -0.0026 | 0.0059 | -1.2183
8191 | 3871 | 2.116 | 0 | 0 | 0 | 23.6134 | 7.197 | 1.857 | 21.8185 | 0.74952 | -0.0013651 | -0.0013599 | 0.0059 | -0.0099 | 1.49
8201 | 3881 | 2.1131 | 0 | 0 | 0 | 23.5809 | 7.1871 | 1.8471 | 21.8066 | 0.74816 | -0.0013599 | -0.0013547 | -0.0099 | -0.0028 | 4.6685
8211 | 3891 | 2.1103 | 0 | 0 | 0 | 23.5717 | 7.1843 | 1.8443 | 21.802 | 0.74681 | -0.0013547 | -0.0013496 | -0.0028 | -0.0036 | 2.3677
8221 | 3901 | 2.1074 | 0 | 0 | 0 | 23.5599 | 7.1807 | 1.8407 | 21.8086 | 0.74546 | -0.0013496 | -0.0013445 | -0.0036 | -0.0001 | 1.3685
8231 | 3911 | 2.1046 | 0 | 0 | 0 | 23.5595 | 7.1806 | 1.8406 | 21.8146 | 0.74411 | -0.0013445 | -0.0013394 | -0.0001 | -0.0075 | 2.8421
8241 | 3921 | 2.1018 | 0 | 0 | 0 | 23.5349 | 7.1731 | 1.8331 | 21.8163 | 0.74277 | -0.0013394 | -0.0013344 | -0.0075 | -0.0028 | 3.8455
8251 | 3931 | 2.099 | 0 | 0 | 0 | 23.5258 | 7.1703 | 1.8303 | 21.8146 | 0.74144 | -0.0013344 | -0.0013294 | -0.0028 | -0.0046 | 2.7805 | -0.010498 | -0.010192 | -0.0348 | -0.0444 | 3.8434
8261 | 3941 | 2.0962 | 0 | 0 | 0 | 23.5107 | 7.1657 | 1.8257 | 21.8142 | 0.74011 | -0.0013294 | -0.0013244 | -0.0046 | -0.0018 | 2.4077
8271 | 3951 | 2.0934 | 0 | 0 | 0 | 23.5048 | 7.1639 | 1.8239 | 21.8206 | 0.73879 | -0.0013244 | -0.0013195 | -0.0018 | -0.0015 | 1.2477
8281 | 3961 | 2.0906 | 0 | 0 | 0 | 23.4998 | 7.1624 | 1.8224 | 21.8237 | 0.73747 | -0.0013195 | -0.0013146 | -0.0015 | -0.0075 | 3.4253
8291 | 3971 | 2.0879 | 0 | 0 | 0 | 23.4752 | 7.1549 | 1.8149 | 21.8119 | 0.73615 | -0.0013146 | -0.0013097 | -0.0075 | -0.0053 | 4.8745
8301 | 3981 | 2.0852 | 0 | 0 | 0 | 23.4578 | 7.1496 | 1.8096 | 21.8108 | 0.73484 | -0.0013097 | -0.0013048 | -0.0053 | -0.0017 | 2.6723
8311 | 3991 | 2.0824 | 0 | 0 | 0 | 23.4523 | 7.1479 | 1.8079 | 21.8108 | 0.73354 | -0.0013048 | -0.0013 | -0.0017 | -0.0081 | 3.7714
8321 | 4001 | 2.0797 | 0 | 0 | 0 | 23.4257 | 7.1398 | 1.7998 | 21.7809 | 0.73224 | -0.0013 | -0.0012952 | -0.0081 | -0.0043 | 4.7727
8331 | 4011 | 2.077 | 0 | 0 | 0 | 23.4116 | 7.1355 | 1.7955 | 21.7781 | 0.73094 | -0.0012952 | -0.0012904 | -0.0043 | -0.0014 | 2.2004 | -0.010192 | -0.0099 | -0.0444 | -0.0488 | 4.647
8341 | 4021 | 2.0744 | 0 | 0 | 0 | 23.407 | 7.1341 | 1.7941 | 21.7677 | 0.72965 | -0.0012904 | -0.0012857 | -0.0014 | -0.0097 | 4.3207
8351 | 4031 | 2.0717 | 0 | 0 | 0 | 23.3752 | 7.1244 | 1.7844 | 21.7672 | 0.72837 | -0.0012857 | -0.001281 | -0.0097 | -0.0035 | 5.1341
8361 | 4041 | 2.069 | 0 | 0 | 0 | 23.3637 | 7.1209 | 1.7809 | 21.7572 | 0.72709 | -0.001281 | -0.0012763 | -0.0035 | -0.0036 | 2.7766
8371 | 4051 | 2.0664 | 0 | 0 | 0 | 23.3519 | 7.1173 | 1.7773 | 21.7575 | 0.72581 | -0.0012763 | -0.0012716 | -0.0036 | -0.0072 | 4.2441
8381 | 4061 | 2.0638 | 0 | 0 | 0 | 23.3282 | 7.1101 | 1.7701 | 21.7611 | 0.72454 | -0.0012716 | -0.001267 | -0.0072 | -0.0039 | 4.3678
8391 | 4071 | 2.0612 | 0 | 0 | 0 | 23.3154 | 7.1062 | 1.7662 | 21.761 | 0.72327 | -0.001267 | -0.0012623 | -0.0039 | -0.0114 | 6.06
8401 | 4081 | 2.0586 | 0 | 0 | 0 | 23.278 | 7.0948 | 1.7548 | 21.7466 | 0.72201 | -0.0012623 | -0.0012578 | -0.0114 | -0.0037 | 5.9807
8411 | 4091 | 2.056 | 0 | 0 | 0 | 23.2659 | 7.0911 | 1.7511 | 21.7374 | 0.72075 | -0.0012578 | -0.0012532 | -0.0037 | -0.0058 | 3.7865 | -0.0099 | -0.0096208 | -0.0488 | -0.0483 | 4.9755
8421 | 4101 | 2.0534 | 0 | 0 | 0 | 23.2469 | 7.0853 | 1.7453 | 21.7417 | 0.7195 | -0.0012532 | -0.0012487 | -0.0058 | -0.0046 | 4.1552
8431 | 4111 | 2.0508 | 0 | 0 | 0 | 23.2318 | 7.0807 | 1.7407 | 21.7416 | 0.71825 | -0.0012487 | -0.0012441 | -0.0046 | -0.0064 | 4.4153
8441 | 4121 | 2.0483 | 0 | 0 | 0 | 23.2108 | 7.0743 | 1.7343 | 21.7311 | 0.717 | -0.0012441 | -0.0012397 | -0.0064 | -0.0077 | 5.6787
8451 | 4131 | 2.0458 | 0 | 0 | 0 | 23.1855 | 7.0666 | 1.7266 | 21.7266 | 0.71577 | -0.0012397 | -0.0012352 | -0.0077 | -0.0071 | 5.9793
8461 | 4141 | 2.0432 | 0 | 0 | 0 | 23.1622 | 7.0595 | 1.7195 | 21.7222 | 0.71453 | -0.0012352 | -0.0012308 | -0.0071 | -0.0042 | 4.5782
8471 | 4151 | 2.0407 | 0 | 0 | 0 | 23.1484 | 7.0553 | 1.7153 | 21.7186 | 0.7133 | -0.0012308 | -0.0012264 | -0.0042 | -0.0066 | 4.3989
8481 | 4161 | 2.0382 | 0 | 0 | 0 | 23.1268 | 7.0487 | 1.7087 | 21.714 | 0.71207 | -0.0012264 | -0.001222 | -0.0066 | -0.0064 | 5.3095
8491 | 4171 | 2.0357 | 0 | 0 | 0 | 23.1058 | 7.0423 | 1.7023 | 21.7094 | 0.71085 | -0.001222 | -0.0012176 | -0.0064 | -0.0037 | 4.1361 | -0.0096208 | -0.0093537 | -0.0483 | -0.036 | 4.4263
8501 | 4181 | 2.0332 | 0 | 0 | 0 | 23.0936 | 7.0386 | 1.6986 | 21.6951 | 0.70963 | -0.0012176 | -0.0012133 | -0.0037 | -0.0111 | 6.0992
8511 | 4191 | 2.0308 | 0 | 0 | 0 | 23.0572 | 7.0275 | 1.6875 | 21.6888 | 0.70842 | -0.0012133 | -0.001209 | -0.0111 | -0.0019 | 5.3534
8521 | 4201 | 2.0283 | 0 | 0 | 0 | 23.051 | 7.0256 | 1.6856 | 21.686 | 0.70721 | -0.001209 | -0.0012047 | -0.0019 | -0.0081 | 4.1523
8531 | 4211 | 2.0259 | 0 | 0 | 0 | 23.0244 | 7.0175 | 1.6775 | 21.685 | 0.70601 | -0.0012047 | -0.0012004 | -0.0081 | -0.0044 | 5.1919
8541 | 4221 | 2.0235 | 0 | 0 | 0 | 23.01 | 7.0131 | 1.6731 | 21.6825 | 0.70481 | -0.0012004 | -0.0011962 | -0.0044 | -0.0105 | 6.2263
8551 | 4231 | 2.021 | 0 | 0 | 0 | 22.9755 | 7.0026 | 1.6626 | 21.6728 | 0.70361 | -0.0011962 | -0.0011919 | -0.0105 | -0.0052 | 6.5664
8561 | 4241 | 2.0186 | 0 | 0 | 0 | 22.9585 | 6.9974 | 1.6574 | 21.6694 | 0.70242 | -0.0011919 | -0.0011878 | -0.0052 | -0.0034 | 3.6113
8571 | 4251 | 2.0162 | 0 | 0 | 0 | 22.9473 | 6.994 | 1.654 | 21.6724 | 0.70123 | -0.0011878 | -0.0011836 | -0.0034 | -0.0067 | 4.2641 | -0.0093537 | -0.009098 | -0.036 | -0.0136 | 2.6555
8581 | 4261 | 2.0138 | 0 | 0 | 0 | 22.9253 | 6.9873 | 1.6473 | 21.671 | 0.70005 | -0.0011836 | -0.0011794 | -0.0067 | -0.0033 | 4.2269
8591 | 4271 | 2.0115 | 0 | 0 | 0 | 22.9145 | 6.984 | 1.644 | 21.6671 | 0.69887 | -0.0011794 | -0.0011753 | -0.0033 | -0.0051 | 3.57
8601 | 4281 | 2.0091 | 0 | 0 | 0 | 22.8978 | 6.9789 | 1.6389 | 21.658 | 0.69769 | -0.0011753 | -0.0011712 | -0.0051 | -0.0066 | 4.9884
8611 | 4291 | 2.0068 | 0 | 0 | 0 | 22.8761 | 6.9723 | 1.6323 | 21.6521 | 0.69652 | -0.0011712 | -0.0011671 | -0.0066 | 0.001 | 2.3836
8621 | 4301 | 2.0044 | 0 | 0 | 0 | 22.8794 | 6.9733 | 1.6333 | 21.6578 | 0.69535 | -0.0011671 | -0.0011631 | 0.001 | -0.0051 | 1.7687
8631 | 4311 | 2.0021 | 0 | 0 | 0 | 22.8627 | 6.9682 | 1.6282 | 21.6752 | 0.69419 | -0.0011631 | -0.001159 | -0.0051 | -0.0042 | 4.0037
8641 | 4321 | 1.9998 | 0 | 0 | 0 | 22.8489 | 6.964 | 1.624 | 21.1827 | 0.69303 | -0.001159 | -0.001155 | -0.0042 | -0.006 | 4.4106
8651 | 4331 | 1.9975 | 0 | 0 | 0 | 22.8292 | 6.958 | 1.618 | 21.2599 | 0.69188 | -0.001155 | -0.001151 | -0.006 | -0.0034 | 4.0724 | -0.009098 | -0.68278 | -0.0136 | -1.6044 | 1.5061
8661 | 4341 | 1.9952 | 0 | 0 | 0 | 22.818 | 6.9546 | 1.6146 | 21.3241 | 0.69073 | -0.001151 | -0.001147 | -0.0034 | -0.0072 | 4.6184
8671 | 4351 | 1.9929 | 0 | 0 | 0 | 22.7944 | 6.9474 | 1.6074 | 21.4537 | 0.68958 | -0.001147 | -0.0011431 | -0.0072 | -0.0011 | 3.6151
8681 | 4361 | 1.9906 | 0 | 0 | 0 | 22.7908 | 6.9463 | 1.6063 | 21.6426 | 0.68844 | -0.0011431 | -0.0011391 | -0.0011 | 0 | 0.48033
8691 | 4371 | 1.9883 | 0 | 0 | 0 | 22.7908 | 6.9463 | 1.6063 | 21.7835 | 0.6873 | -0.0011391 | -0.0011352 | 0 | 0.0016 | -0.70591
8701 | 4381 | 1.9861 | 0 | 0 | 0 | 22.7961 | 6.9479 | 1.6079 | 21.8896 | 0.68616 | -0.0011352 | -0.0011313 | 0.0016 | -0.0012 | -0.17224
8711 | 4391 | 1.9838 | 0 | 0 | 0 | 22.7921 | 6.9467 | 1.6067 | 21.9496 | 0.68503 | -0.0011313 | -0.0011275 | -0.0012 | -0.0012 | 1.0625
8721 | 4401 | 1.9816 | 0 | 0 | 0 | 22.7882 | 6.9455 | 1.6055 | 22.0049 | 0.6839 | -0.0011275 | -0.0011236 | -0.0012 | -0.0011 | 1.0216
8731 | 4411 | 1.9794 | 0 | 0 | 0 | 22.7846 | 6.9444 | 1.6044 | 22.05 | 0.68278 | -0.0011236 | -0.0011198 | -0.0011 | 0.0004 | 0.30974 | -0.68278 | 0 | -1.6044 | 0 | #DIV/0!
8741 | 4421 | 1.9772 | 0 | 0 | 0 | 22.7859 | 6.9448 | 1.6048 | 22.0802 | 0.68166 | -0.0011198 | -0.001116 | 0.0004 | 0.0013 | -0.76173
8751 | 4431 | 1.9749 | 0 | 0 | 0 | 22.7902 | 6.9461 | 1.6061 | 22.1135 | 0.68054 | -0.001116 | -0.68054 | 0.0013 | -1.6061 | -1.1591

## Hydraulic Paramaters
Aquifer Hydraulic Paramaters | [12 empty] | Well Hydraulic Paramaters
| Theis Curve-Matching Method |  |  |  | Cooper-Jacob Straight Line Method |  |  |  | Theis Recovery Method |  |  |  |  | Long Term Yield (100 day method)
|  | Equations |  |  |  | Equations |  |  |  | Equations |  |  |  |  | Equations
| T = ( Q * W (u) ) / ( 4 * pi * s ) |  |  |  | T = ( 2.3 * Q ) / ( 4 * pi * slope ) |  |  |  | T = ( 2.3 * Q ) / ( 4 * pi * slope ) |  |  |  |  | Q100 = SAD*SC = 0.7*Available DD*Q/100 Day DD
Available DD = SWL-Water bearing fracture
|  | Variables |  |  |  | Variables |  |  |  | Variables |  |  |  |  | Variables
| Note: Taken from radial flow time segment |  |  |  | Note: Taken from radial flow time segment |  |  |  | Note: Taken from radial flow time segment |  |  |  |  | Q (Discharge Rate) |  | 70.84 | m3/day
[14 empty] | 100 Day DD |  | 28 | m
| Match Point |  |  |  | Slope is for 1 log10 cycle of time |  |  |  | Slope is for 1 log10 cycle of time |  |  |  |  | Well Depth |  | 38.1 | m
| s (Drawdown) |  | 8.7 | m | Q (Discharge Rate) |  | 70.84 | m3/day | [5 empty] | SWL |  | 5.34 | m
| t (time) |  |  |  | slope (ds/dlog(t)) |  | 4.8 | m | Q (Discharge Rate) |  | 70.84 | m3/day |  | Water bearing fracture |  | 31 | m
| W(u) |  | 3.5 | [5 empty] | slope (ds/dlog(t/t')) |  | 4.7 | m
1/u
| Q ((Discharge Rate) |  | 70.84 | m3/day
| T (Transmissivity) |  | 2.268 | m2/day | T (Transmissivity) |  | 2.701 | m2/day | T (Transmissivity) |  | 2.759 | m2/day |  | Q100 |  | 45.4439 | m3/day
Match Point
100 Day Drawdown = 28 m
100 Days
ds/d(log(t/t')) = 4.7